## Introduction
PlantPAx 5.30 checklist
About This Publication | This publication is the PlantPAx 5.30 checklist
For more information see:PlantPAx Distributed Control System Configuration and Implementation, PROCES-UM100
PROCES-UM100
Important: Rockwell Automation is not responsible for any content or format changes made by other parties after downloading this spreadsheet file. The original file can be re-downloaded at any time.
TIP: When you search for information in a spreadsheet, set the search options to search the workbook, rather than the current sheet (tab).
Allen-Bradley, CompactLogix, GuardLogix, Logix 5000, Rockwell Automation, and Studio 5000 are trademarks of Rockwell Automation, Inc. EtherNet/IP is a trademark of ODVA, Inc. Trademarks not belonging to Rockwell Automation are property of their respective companies.

## Instructions
Use the checklists on each to tab to verify and document that your system design aligns with PlantPAx system recommendations
For more information, see Appendix C in the PlantPAX Configuration and Implementation Guide, PROCES-UM100.
Checklist Icons
Icon | Description
Failure – requires corrective action
Warning – corrective action is recommended
Passed – aligns with system recommendations
Not applicable – not completed or does not apply
Information only – documentation or calculation purposes only
A successful PlantPAx system design has completed checklists that do not have any failures and all warnings are addressed. You can attach reports to a checklist for categories that are information only.
Assumptions
1 | Your PlantPAx system is operable (for example, the HMI application is running and the latest operating system patches are installed).
2 | You have defined a range of IP addresses for the DHCP server in the domain, if applicable for your system.
3 | You have created groups and assigned users in the domain controller.
4 | If you are using virtualization, the VMware vSphere Client software is installed and connected to a vCenter server or ESXi (hypervisor) host.

## Design Recommendations
Application Checklist | [6 empty] | Results
System Name:
Design Element |  | Observed Value | Results | Notes |  |  | Pass | Warning | Fail | Explain if <> Pass
System ID | PlantPAx Core software bundle |  | 1 |  |  | 1 | Catalog number of the PlantPAx core software bundle | No
| Inventory agent |  | 1 |  |  | 1 | The System Integrator generated the .raai file via the FactoryTalk AssectCentre inventory agent | No
| MyEquipment portal |  | 1 |  |  | 1 | The System Integrator registered to the system, and provided directions on how to access the MyEquipment portal | No
Controller Considerations | Controller name |  | 1 |  |  | 1 | ACD filename = Controller name = Shortcut name | ACD filename <> Controller name <> Shortcut name
| Routine / Tag Names |  | 1 |  |  | 1 | Yes Control strategy and instrument naming schemes follow ISA 5.x standards | No
| Controller Organizer |  | 1 |  |  | 1 | Yes Control programs are organized to contain logic based on required execution rate | No
| Logical Organizer |  | 1 |  |  | 1 | Yes Folder name = Primary Graphic Display name | No
| Controller Routines | Routine Name | 1 |  |  | 1 | Yes Routine name = Device name | No
|  | One Routine per Device | 1 |  |  | 1 | Yes One Routine per device | No
|  | Standard PlantPAx Control Strategies | 1 |  |  | 1 | Yes Each device (such as motor, valve, PID) uses a standard PlantPAx control strategy programmed in Function Block diagram | No
|  | Control logic External to Device Routine | 1 |  |  | 1 | Yes Supervisory or device control logic is external to the device control strategies. This reduces variability among strategies and minimizes the risk of replicating modified control strategies | No
| Controller Programs |  | 1 |  |  | 1 | Yes The routines in each program have same primary display | No
Library Considerations | Process Library Objects |  | 1 |  |  | 1 | Yes The process library objects were not modified | No
Alarm Considerations | Standards |  | 1 |  |  | 1 | Yes Follow ISA 18.2 standards for alarm management | No Do not follow ISA 18.2 standards for alarm management
| ALMA / ALMD Alarm Instructions |  | 1 |  |  | 1 | Yes Use tag-based alarms and FTAE alarms | No Extensive use of ALMA/AMLD
I/O Considerations | RPI |  | 1 |  |  | 1 | Yes RPI scan time ~ 1/2 Associated Logic Scan time | No RPI scan time <> 1/2 Associated Logic Scan time
| Consistent I/O Methodology |  | 1 |  |  | 1 | Yes I/O connection method is one of the following: I/O mapping, direct I/O connection, aliasing, or program parameters | No
HMI Considerations | Graphical Framework |  | 1 |  |  | 1 | Yes Use Graphical Framework | No Do not use Graphical Framework
| Follow ISA 101 Style Guide |  | 1 |  |  | 1 | Yes Use ISA 101 | No Do not use ISA 101
| Naming Conventions |  | 1 |  |  | 1 | Yes Name displays are based on Logical Organizer hierarchy | No Do not name displays based on Logical Organizer hierarchy
| Design for the Future |  | 1 |  |  | 1 | Yes Future development considered in application and area names | No Future development not considered in application and area names
Name |  | Signature |  | Date | 2025-08-27 13:46
1
2

## System Infrastructure
System Infrastructure Checklist | [8 empty] | Results
System Name:
Design Element |  | Observed Value |  |  | Results | Notes |  |  | Pass | Warning | Fail
Hardware | BIOS Power saving options disabled ? |  |  |  | 1 |  |  | 1 | Yes |  | No Correct and reverify.
Virtualization | Using Virtualization ? |  |  |  | 1 |  |  | 1 | Yes
Hypervisor(s) | CPU Utilization |  |  | % | 0 |  |  |  | CPU utilization is within 50% of used resources. |  | CPU utilization exceeds system recommendations
| Memory |  |  | % | 0 |  |  |  | Memory utilization is within 50% of used resources. |  | Memory utilization exceeds system recommendations.
| CPU Utilization |  |  | % | 0 |  |  |  | CPU utilization is within 50% of used resources. |  | CPU utilization exceeds system recommendations
| Memory |  |  | % | 0 |  |  |  | Memory utilization is within 50% of used resources. |  | Memory utilization exceeds system recommendations.
| CPU Utilization |  |  | % | 0 |  |  |  | CPU utilization is within 50% of used resources. |  | CPU utilization exceeds system recommendations
| Memory |  |  | % | 0 |  |  |  | Memory utilization is within 50% of used resources. |  | Memory utilization exceeds system recommendations.
| CPU Utilization |  |  | % | 0 |  |  |  | CPU utilization is within 50% of used resources. |  | CPU utilization exceeds system recommendations
| Memory |  |  | % | 0 |  |  |  | Memory utilization is within 50% of used resources. |  | Memory utilization exceeds system recommendations.
Domain | All Servers and Workstations are on the same Domain |  |  |  | 1 |  |  | 1 | Yes | No If you do not intend to use a domain, make sure that your system has fewer than 10 servers and workstations. You also are responsible to make sure that time synchronization, security policies, and user configuration are manually shared across all computers on the system.
Network | Bandwidth Utiliz % |  |  |  | 0 |  |  |  | Bandwidth < 50% |  | 50% and up is a fail Review and verify the network architecture for system compliance or call a Rockwell Automation® Support representative.
| Packet Error Rate |  |  |  | -1 |  |  |  | Error rate = 0 |  | Error rate is greater than 0. If the error rate is not zero, but not increasing, we recommend a reset. Review and verify the network architecture for system compliance or call a Rockwell Automation Support representative.
| Temperature OK |  |  |  | 1 |  |  | 1 | Yes |  | No Rectify the environment and verify the network design. You also can call a Rockwell Automation Support representative.
| CPU Utilization % |  |  |  | 0 |  |  |  | CPU use <= 50% |  | CPU allocation is greater than 50%. Review and verify the network architecture for system compliance or call a Rockwell Automation Support representative.
| Memory Utilization % |  |  |  | 0 |  |  |  | Memory use <= 50% |  | Memory usage is greater than 50%. Review and verify the network architecture for system compliance or call a Rockwell Automation Support representative.
Servers and Workstations | Computer Name: | System Role |  |  |  | Page 1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
Name |  |  | Signature |  |  | Date | 2025-08-27 13:46
System Infrastructure Checklist
Servers and Workstations | Computer Name: | System Role |  |  |  | Page 2
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
Name |  |  | Signature |  |  | Date | 2025-08-27 13:46

## <Server or WS name>
Server or Workstation - Checklist | [9 empty] | Results
System Name: |  |  |  | Computer Name:
Design Element |  | Observed Value |  |  | Results | Notes |  |  |  | Pass | Warning | Fail
Operating System | Windows firewall being used |  |  |  | 1 |  |  | 1 |  | Yes | No Write in the Notes column what solution is providing firewall protection or why it was disabled on this system.
| Operating System valid |  |  |  | 1 |  |  | 1 |  | Yes | No Write in the Notes column what solution is providing firewall protection or why it was disabled on this system.
| Rockwell Software patches applied |  |  |  | 1 |  |  | 1 |  | Yes | No Write the Patch Validator version or date last used in the Notes section. When time permits, use the tool to perform a patch roll-up.
| NIC Power saving options disabled |  |  |  | 1 |  |  | 1 |  | Yes | No Correct and reverify
| Windows Power saving options disabled |  |  |  | 1 |  |  | 1 |  | Yes | No Correct and reverify
| Desktop Experience enabled in RDS Servers |  |  |  | 1 |  |  | 1 |  | Yes | No Correct and reverify
| Adjust for best performance is selected |  |  |  | 1 |  |  | 1 |  | Yes | No Correct and reverify
| Data Execution Prevention Windows only |  |  |  | 1 |  |  | 1 |  | Yes | No Correct and reverify
| User Account Control Never notify |  |  |  | 1 |  |  | 1 |  | Yes | No Correct and reverify
| Windows Automatic Update is disabled |  |  |  | 1 |  |  | 1 |  | Yes | No Correct and reverify
| Event Viewer is not presenting errors |  |  |  | 1 |  |  | 1 |  | Yes |  | No Correct and reverify All errors must be corrected before you can proceed
| NSLookup resolved |  |  |  | 1 |  |  | 1 |  | Yes | No Correct and reverify
Performance | Performance Monitor | [8 empty] | Yes Generate a performance report
Basic System Checks | OS Checks |  |  |  | 1 |  |  | 1 |  | Passed |  | Not Passed Review your computer configuration and make changes or upgrades to make sure that servers and workstations are within recommended limits.
| Disk Checks |  |  |  | 1 |  |  | 1 |  | Passed |  | Not Passed Address any drive issues on the computer or server that did not pass and reverify.
| Security Center Tests |  |  |  | 1 |  |  | 1 |  | Passed | Not Passed Review security settings and reverify if you made changes.
| System Service Checks |  |  |  | 1 |  |  | 1 |  | Passed |  | Not Passed Address any system service issues on the computer or server that did not pass and reverify
| Hardware Device Driver Checks |  |  |  | 1 |  |  | 1 |  | Passed |  | Not Passed Address any device driver issues on the computer or server that did not pass and reverify
Resource Overview | CPU (%) | 0 |  |  | 1 |  |  | 1 | 0 | Passed |  | Not Passed Resize the system or split the servers for more CPU in a virtual environment.
| Network (%) | 0 |  |  | 1 |  |  | 1 | 0 | Passed The busiest network adapter is < 50% |  | Not Passed Reevaluate the network traffic and reverify.
| Disk (/sec) | 0 |  |  | 1 |  |  | 1 | 1 | Passed |  | Not Passed Replace the disk with a higher throughput or create additional disks.
| Memory (%) | 0 |  |  | 1 |  |  | 1 | 0 | Passed |  | Not Passed Increase the memory capacity.
Name |  |  | Signature |  |  | Date | 2025-08-27 13:46

## System Architecture
System Architecture Checklist | [8 empty] | Results
System Name:
Design Element |  | Observed Value |  |  | Results | Notes |  |  | Pass | Warning | Fail
FactoryTalk® View Application Design | Number of HMI Servers |  |  |  | 0 |  |  |  | Number of servers <= 10 per system |  | Number > 10 maximum servers per system. Reduce the number of HMI servers in the system tree of the FactoryTalk Administration Console window.
| Number of Alarm Servers |  |  |  | 0 |  |  |  | Number of servers <= 10 per system |  | Number > 10 maximum servers per system. Reduce the number of alarm servers in the system tree of the FactoryTalk Administration Console window.
| Number of Data Servers |  |  |  | 0 |  |  |  | Number of data servers (FactoryTalk Linx + OPC UA) <= 10 per system |  | Number > 10 maximum servers per system. Reduce the number of data servers in the system tree of the FactoryTalk Administration Console window.
| Each Server is in its own Area |  |  |  | 1 |  |  | 1 | Yes |  | No Correct the area organization in the tree structure of the application
FactoryTalk View HMI Servers (PASS) | Uses Data Logging |  |  |  | 1 |  |  | 1 | No Use FactoryTalk Historian software for data collection | Yes Use data logs for short-term storage only. Manage the data log size and segregate the hard disk drive that collects the data so PASS performance is not affected.
| Dedicated Servers ? |  |  |  | 1 |  |  | 1 | Yes indicates all computers host no more than one HMI server. |  | No indicates that some computers host multiple HMI servers. Put the computer host name in the Notes column.
| Redundancy Status |  |  |  | 1 |  |  | 1 | Synched | Not synched Synchronization is not a necessary configuration for all primary and secondary servers, we recommend that you test the switchover configuration for all servers.
FactoryTalk Alarm and Event Servers (PASS) | Dedicated Servers ? |  |  |  | 1 |  |  | 1 | Yes indicates all computers host no more than one Alarm and Event server. |  | No indicates that some computers host multiple A&E servers. Put the computer host name in the Notes column.
| Redundancy Status |  |  |  | 1 |  |  | 1 | Synched | Not synched Synchronization is not a necessary configuration for all primary and secondary servers, we recommend that you test the switchover configuration for all servers.
| Alarm & Event History Enabled ? |  |  |  | 1 |  |  | 1 | Yes | No
FactoryTalk View Data Servers (PASS) | Max Number of FTLinx Instances on any PASS | 0 |  |  | 0 |  |  |  | FactoryTalk Linx supports 2 data server instances on any one computer. |  | >2 indicates that there are too many data servers on a computer. Put the computer host name in the Notes column.
| Dedicated Servers for OPC UA ? |  |  |  | 1 |  |  | 1 | Yes indicates any computers hosting a OPC UA server do not have any additional data or HMI servers |  | No You must not host multiple servers on a single OPC UA PASS computer.
| Redundancy Status |  |  |  | 1 |  |  | 1 | Synched | Not synched Synchronization is not a necessary configuration for all primary and secondary servers, we recommend that you test the switchover configuration for all servers.
| Alarm & Event History Enabled ? |  |  |  | 1 |  |  | 1 | Yes | No
FactoryTalk AssetCentre (AppServ-Asset Mgmt) | Number of Assets | 0 |  |  | 1 |  |  |  | Licensing determines the allowable number of assets. A base license includes 10 assets.
| Number Disaster Recovery (DR) Assets | 0 |  |  | 0 |  |  |  | Number of controllers that are configured for Disaster Recovery | Reduce the number of assets or increase number of agents. Upload assets less frequently
| Number of Agents | 0 | [6 empty] | Number of agents
| How often DR Assets configured to upload | 0 |  | days |  |  |  |  | Number of days between asset uploads
FactoryTalk Historian SE (AppServ-Info) | Points in Use | 0 |  |  | 0 |  |  |  | Number of points is less than the points limit. | Number of points exceeds the points limit. Write in the Notes section whether you need to add licenses or reduce the number of configured points in the Historian software.
| Points Limit | 0 |  |  | 1 |  |  |  | This value sets a benchmark that can be compared to future server results. The comparison can identify a potential issue with too many points per license.
| Fastest Scan Class |  |  | sec | 1 |  |  | 1 | Meets system performance | Scan rate is faster than 1 second. Scanning data at a rate faster than the data is changing wastes network and computer resources and unnecessarily uses network bandwidth. Reduce the speed at which the data is being scanned.
| Number of Interfaces | 0 |  |  | 0 |  |  |  | Number of FactoryTalk Live Data interfaces For a redundant interface, Historian Points in Use cannot exceed 20,000 tags per second | Exceeded 20,000 tags per second. Add additional interfaces or choose slower scan class
| Buffering Enabled and Running |  |  |  | 1 |  |  | 1 | Yes Buffering is recommended to maintain data collection in the event the connection to the server is lost | No
| Unit Fail Over Enabled and Running |  |  |  | 1 |  |  | 1 | Yes All of the interfaces have unit fail over enabled and are running | No
| Collective Enabled and Running |  |  |  | 1 |  |  | 1 | Yes A collective if properly configured for redundant systems | No
Name |  |  | Signature |  |  | Date | 2025-08-27 13:46
0

## <PASS>
PASS Checklist | [12 empty] | Results
System Name: |  |  |  | Server Name:
Design Element |  | Observed Value |  |  | Results | Notes | [6 empty] | Pass | Warning | Fail
FactoryTalk View SE (HMI) | Number of Displays | 0 |  | 1 | 0 |  |  | 0 | 0 | 0 | 0 |  | Total number of displays does not exceed the display license |  | If the total number of displays exceeds the display license, delete any unnecessary displays from the HMI server or update the license
| Total Tags on Server | 0 |  |  | 1 | [7 empty] | Design displays meet recommendations. | Consider simplifying displays to use less tags, expressions, and/or global objects. | Simplify displays to use less tags, expressions, and/or global objects.
| Unique Tags | Yellow Warning |  |  | 1 | [6 empty] | 1
|  | Red Error |  |  | 1 | [6 empty] | 1
| Expressions | Yellow Warning |  |  | 1 | [6 empty] | 1
|  | Red Error |  |  | 1 | [6 empty] | 1
| Global Objects | Yellow Warning |  |  | 1 | [6 empty] | 1
| Display Type | Yellow Warning |  |  | 1 | [6 empty] | 1 | Display Type = Replace Display Cache = No Always Updating + not checked | Correct and reverify
| Display Cache | Yellow Warning |  |  | 1 | [6 empty] | 1
| Always Updating | Yellow Warning |  |  | 1 | [6 empty] | 1
| Graphic Update Rate | Yellow Warning |  |  | 1 | [6 empty] | 1 | Update rate within recommendation | Faster rates possibly impact the server performance | Faster rates have impact on the server performance
|  | Red Error |  |  | 1 | [6 empty] | 1
FactoryTalk Alarms and Events | Number of Server Tag-Based Alarms (FTAE Alarm Server) |  |  |  | 0 | [7 empty] | Number of Server Tag-based alarms does not exceed 20,000 per server |  | Exceeds 20,000 per server. Simplify the alarm system by deleting alarms or move alarms to another PASS.
| Total Items (Server Tag-based) |  |  |  | 1 | [7 empty] | Total number of items on the Tag Update Rates of the FactoryTalk Alarm and Event Setup dialog box
| Fastest Update Rate (Server Tag-based) |  |  | sec | 1 | [6 empty] | 1 | Update rate meets recommendation of 1 second. Default is 2 seconds to help reduce load on the system. |  | Change any alarm update rate to 1 second or slower to reduce the load on the alarm server
| All tags addressed from the local data server ? (Server Tag-based) |  |  |  | 1 | [6 empty] | 1 | The alarm server references the data server hosted on the same computer |  | Move non-compliant alarms to the appropriate alarm server associated with the data server
| Number of Logix Tag-Based Alarms (FTLinx Instance 1) |  |  |  | 0 | [7 empty] | Number of Logix Tag-based alarms does not exceed 15,000 per instance of FTLinx |  | Exceeds 15,000 per instance. Simplify the alarm system by deleting alarms or move alarms to another PASS.
| Number of Logix Tag-Based Alarms (FTLinx Instance 2) |  |  |  | 0 | [7 empty] | Number of Logix Tag-based alarms does not exceed 15,000 per instance of FTLinx |  | Exceeds 15,000 per instance. Simplify the alarm system by deleting alarms or move alarms to another PASS.
| Total Alarms (Server Tag-based + Logix Tag-based) | 0 |  |  | 0 | [7 empty] | Number of total alarms (Server + Logix) does not exceed 30,000 per PASS |  | Exceeds 30,000 per PASS. Simplify the alarm system by deleting alarms or move alarms to another PASS.
Data Server (FactoryTalk Linx Instance 1) | Memory Usage |  |  | MB | 0 | Using Data Server ? | [5 empty] | 0 | Memory Usage is acceptable | Reduce load on data server
| Shortcut (5x80) | # Polled Data Items | Average Packets per Second | Avg Pcket Response Time | Results
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
Shortcut (5x70)
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
| Total | 0 | 0 | 0 | 0 | [6 empty] | 0 | Data Server is not overloaded | Reduce overall load on Data Server
Data Server (FactoryTalk Linx Instance 2) | Memory Usage |  |  | MB | 0 | Using Data Server ? | [5 empty] | 0 | Memory usage is acceptable | Reduce load on data server
| Shortcut (5x80) | # Polled Data Items | Average Packets per Second | Avg Pcket Response Time | Results
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
Shortcut (5x70)
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
[5 empty] | 0 | [6 empty] | 0 | Shortcut is not overloaded | Reduce load on controller
| Total | 0 | 0 | 0 | 0 | [6 empty] | 0 | Data Server is not overloaded | Reduce overall load on Data Server
FactoryTalk Linx OPC UA Connector | Using OPC UA Connector ? |  |  |  | 1 | [6 empty] | 1 | PASS is dedicated for OPC UA and no other servers (HMI, Alarm, or Data) are present on this PASS computer. | PASS is not dedicated for OPC UA. If this worksheet indicates other servers (HMI, Alarm, or Data) are active, a warning is displayed
| Number of OPC UA connections | 0 |  |  | 0 | [7 empty] | Connector is not overloaded | Reduce overall load on connector
| FactoryTalk Live Data Active Tags | 0 |  |  | 0 | [7 empty] | Connector is not overloaded | Reduce overall load on connector
| FactoryTalk Live Data Tag Updates/sec | 0 |  |  | 0 | [7 empty] | Connector is not overloaded | Reduce overall load on connector
| Total OPC UA Alarms and Conditions | 0 |  |  | 0 | [7 empty] | The total number of alarms configured across all connected OPC UA servers is ≤ 5000. | The total number of alarms across all OPC UA servers is > 5000. Consider reducing the total number of OPC UA alarms.
DataLogPro | Total DataLogPro tags | 0 |  |  | 0 | [7 empty] | The total number of DataLogPro tags is ≤ 50,000. | The total number of DataLogPro tags is > 50,000. Consider reducing the total number of tags.
Name |  |  | Signature |  |  | Date | 2025-08-27 13:46

## <Controller> 5x80
Controller 5x80 Checklist | [8 empty] | Results
System Name: |  |  |  | Controller Name:
Design Element |  | Observed Value |  |  | Results | Notes |  |  | Pass | Warning | Fail
Properties | Shortcut |  |  |  | 1
Firmware
Module
| Redundancy | [6 empty] | 1
CPU Use | Logix Engine |  |  | % | 0 |  |  | 1 | At least 25% free for Redundant Controllers. No restriction for Simplex | Review controller configuration, scan rates, and controller assignments and make changes to fall within recommended limits.
| Communications Core |  |  | % | 0 |  |  |  | At least 40% free | Reduce the amount of HMI traffic to controller. Reduce the number of tag-based alarms on the controller.
| Packet Processing Engine |  |  | % | 0 |  |  |  | At least 25% free | Reduce the amount of I/O connected to controller. Reduce the amount of produced/consumed tags.
Faults | Minor Faults Count |  |  |  | 0 |  |  | 0 | No minor faults |  | Minor faults must be resolved and cleared. After clearing the minor faults, monitor for a period of time (at least several controller scans) before reverifying.
| Task Overlap |  |  |  | 1 |  |  |  | No task overlap |  | A task overlap must be resolved. Make changes such as simplifying programs, lengthening the period, or raising the relative priority of important tasks.
Capacity | Program Memory (blocks) | Available |  | Tot Used % | 0 |  |  |  | Reserve at least 20% | Upgrade controller for more memory or make changes to reduce load.
|  | Used |  | 0 |  |  |  | 1
| Nodes | Max |  | Tot Used % | 0 |  |  |  | Reserve at least 20% | Reduce the number of I/O modules scanned by this controller, make system changes.
|  | Used |  | 0 |  |  |  | 1
Connections | Total % | Current | High Water | Allowed | 0 |  |  |  | Total connections that are used are <75% of the total allowed connections. | Make necessary application changes to reduce the changes below the recommended limit.
Total Connections
| I/O |  |  |  | 0 |  |  | 1
| Produced Tags |  |  |  | 0
| ConsumedTags |  |  |  | 0 |  |  | 0
| Msg/Block Xfer |  |  | N/A | 1
| Incoming |  |  | N/A | 1 |  |  | 0
| Unconn Buffers |  |  |  | 0
| Msg/Block Cache |  |  |  | 0
Time Synchronization | Controller is time synchronized |  |  |  | 1 |  |  | 1 | Yes Time synchronization is configured between the controllers and computers within the system |  | No, A controller can fail to synchronize because of several factors, including: Not configured for time synchronization Lack of network access to a time master Time synchronization settings are configured incorrectly
Task Structure | Only periodic task used |  |  |  | 1 |  |  | 1 | Yes |  | No You must move code in the continuous task to a periodic task. Delete the continuous task.
Controller Alarms | Total # of Logix Tag-based alarms (both IN-USE and NOT) |  |  |  | 0 |  |  |  | Total number of alarms on controller (both IN-USE and NOT) is ≤10,000 | Consider reducing the number of total alarms on controller
| Total # of Logix Tag-based alarms (IN USE only) |  |  |  | 0 |  |  |  | Total number of alarms on controller (IN-USE only) is ≤7,500 |  | Reduce the number of IN-USE alarms on controller
OPC UA | Total OPC UA nodes/sec |  |  |  | 0 |  |  |  | The total number nodes/sec tags is ≤ 50,000. | The total number nodes/sec tags is > 50,000.Consider reducing the amount of OPC UA data.
Name |  |  | Signature |  |  | Date | 2025-08-27 13:46
1
1
1

## <Controller> 5x70
Controller 5x70 Checklist | [8 empty] | Results
System Name: |  |  |  | Controller Name:
Design Element |  | Observed Value |  |  | Results | Notes |  |  | Pass | Warning | Fail
Properties | Shortcut |  |  |  | 1
| Module | [6 empty] | 1
Firmware
| Redundancy | [6 empty] | 1
CPU Use | Free |  |  | % | 1 |  |  |  | At least 50% of free for redundant controllers (in operation) At least 25% free for simplex controllers. |  | Review controller configuration, scan rates, and controller assignments and make changes to fall within recommended limits.
| Total Used |  |  | % | 0
| Periodic Tasks |  |  | % | 1 |  |  |  | % of CPU use to run all the application code in the controller
| Communications |  |  | % |  |  |  |  | % of CPU use that is needed to respond to communication requests
| Motion |  |  | % |  |  |  |  | % CPU use that is needed to execute motion
| Messages |  |  | % |  |  |  |  | % CPU use that is needed to process messages
| Safety |  |  | % |  |  |  |  | % CPU use that is needed to execute safety tasks
| Redundancy |  |  | % |  |  |  |  | % CPU use that is needed to process redundancy
| System |  |  | % |  |  |  |  | % of system resources
Faults | Minor Faults Count |  |  |  | 0 |  |  | 0 | No minor faults |  | Minor faults must be resolved and cleared. After clearing the minor faults, monitor for a period of time (at least several controller scans) before reverifying.
| Task Overlap |  |  |  | 1 |  |  | 1 | No task overlap |  | A task overlap must be resolved. Make changes such as simplifying programs, lengthening the period, or raising the relative priority of important tasks.
Memory | I/O Memory (bytes) | Free |  | Tot Used % | 0 |  |  |  | At least 50% for redundant controllers At least 25% for simplex controllers | Exceeds 50% for redundant controllers Exceeds 25% for simplex controllers Reduce the number of I/O modules scanned by this controller, make system changes.
|  | Used |  | 0 |  |  |  | 0
| Data & Logic (bytes) | Free |  | Tot Used % | 0 |  |  |  | At least 50% for redundant controllers At least 25% for simplex controllers | Exceeds 50% for redundant controllers Exceeds 25% for simplex controllers Upgrade controller for more memory or make changes to reduce load.
|  | Used |  | 0 |  |  |  | 0
Connections | Total % | Current | High Water | Allowed | 0 |  |  |  | Total connections that are used are <50% of the total allowed connections. | Make necessary application changes to reduce the changes below the recommended limit.
Total Connections
| I/O |  |  |  | 0
| Produced Tags |  |  |  | 0
| ConsumedTags |  |  |  | 0
| Msg/Block Xfer |  |  | N/A | 1
| Incoming |  |  | N/A | 1
| Unconn Buffers |  |  |  | 0
| Msg/Block Cache |  |  |  | 0
Time Synchronization | Controller is time synchronized |  |  |  | 1 |  |  | 1 | Yes Time synchronization is configured between the controllers and computers within the system |  | No, A controller can fail to synchronize because of several factors, including: Not configured for time synchronization Lack of network access to a time master Time synchronization settings are configured incorrectly
Task Structure | Only periodic task used |  |  |  | 1 |  |  | 1 | Yes |  | No You must move code in the continuous task to a periodic task. Delete the continuous task.
Name |  |  | Signature |  |  | Date | 2025-08-27 13:46
1
1

## Summary of Changes
Summary of Changes
| Date | Changes
A | June 2024 | First release as an Excel spreadsheet

## FormData (hidden)
| Selection | Historian Scan | AE Scan | System Computers | FTView | Redundancy
1
2 | Yes | 0.05 | 0.1 | Domain Controller | 100 | N/A
3 | No | 0.1 | 0.25 | PASS | 250 | Synched
| N/A | 0.25 | 0.5 | OWS | Unlimited | Not Synched
| Selection | 0.5 | 1 | EWS
1 |  | 1 | 2 | AppServ-OWS/EWS
2 | Passed | 2 | 5 | AppServ-Info (Historian)
3 | Not Passed | 5 | 10 | AppServ-Info (VantagePoint)
|  | 10 | 20 | AppServ-Info (SQL)
| Selection | 60 | 30 | AppServ-Asset
1 |  | 120 | 60 | AppServ-Batch
2 | N/A |  | 120 | IndWS
3 | Yes
4 | No