## Introduction
Process Object Parameters
About This Publication | This publication lists the Process Objects 5.00, 5.10, 5.20, and 5.30
For more information see: Rockwell Automation Library of Process Objects, PROCES-RM200
PROCES-RM200
Important: Rockwell Automation is not responsible for any content or format changes made by other parties after downloading this spreadsheet file. The original file can be re-downloaded at any time.
TIP: When you search for information in a spreadsheet, set the search options to search the workbook, rather than the current sheet (tab).
Allen-Bradley, CompactLogix, GuardLogix, Logix 5000, Rockwell Automation, and Studio 5000 are trademarks of Rockwell Automation, Inc. EtherNet/IP is a trademark of ODVA, Inc. Trademarks not belonging to Rockwell Automation are property of their respective companies.

## Input Parameters
Library Object | Input Parameter | Input / Output | Data Type | Alias For | Default | Style |  |  | Description
raP_Dvc_D4SD | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Ladder Diagram: If the rung-in condition is true, the instruction’s Logic routine executes. If the rung-in condition is false, the instruction’s EnableInFalse routine executes. Function Block Diagram: If true, or not connected, the instruction’s Logic routine executes. If the parameter is exposed as a pin and wired, and the pin is false, the instruction’s EnableInFalse routine executes. Structured Text: No effect. The instruction’s Logic routine executes. | Read Only | 0
raP_Dvc_D4SD | Inp_InitializeReq | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Request to initialize the instruction. The instruction is normally initialized in instruction first run. Use this request when reinitialization is needed. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_OwnerCmd | Input | DINT |  | 0 | Decimal | 0 | 0 | Owner device command (bitmapped): All bits off = None, .10 = Operator Lock, .11 = Operator Unlock, .12 = Program Lock, .13 = Program Unlock, .14 = Acquire Maintenance, .15 = Release Maintenance, .16 = Acquire External, .17 = Release External, .29 = Echo. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_FdbkAData | Input | BOOL |  | 0 | Decimal | 0 | 1 | Feedback A from device. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_FdbkBData | Input | BOOL |  | 0 | Decimal | 0 | 1 | Feedback B from device. | Read/Write | 0 | 0 | Feedback input signals from device. Use the feedback configuration parameters (for example, Cfg_FdbkSt0Check and Cfg_FdbkSt0State) to determine how these inputs are used to determine actual state.
raP_Dvc_D4SD | Inp_FdbkCData | Input | BOOL |  | 0 | Decimal | 0 | 1 | Feedback C from device. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_FdbkDData | Input | BOOL |  | 0 | Decimal | 0 | 1 | Feedback D from device. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_EqpFaultData | Input | BOOL |  | 0 | Decimal | 0 | 1 | Equipment fault from device: 1 = Faulted. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_IOFault | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = I/O communication is faulted, 0 = I/O communication is OK. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_0PermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Permissives are OK, device can be commanded to State 0. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_0NBPermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Non-bypassable permissives are OK, device can be commanded to State 0. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_1PermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Permissives are OK, device can be commanded to State 1. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_1NBPermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Non-bypassable permissives are OK, device can be commanded to State 1. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_2PermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Permissives are OK, device can be commanded to State 2. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_2NBPermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Non-bypassable permissives are OK, device can be commanded to State 2. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_3PermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Permissives are OK, device can be commanded to State 3. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_3NBPermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Non-bypassable permissives are OK, device can be commanded to State 3. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_IntlkOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Interlocks are OK, device can be commanded, 0 = Interlocks are not OK, device is driven to State 0. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_NBIntlkOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Non-bypassable interlocks are OK, device can be commanded, 0 = Interlocks are not OK, device is driven to State 0. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_IntlkAvailable | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Interlock availability is OK, show Sts_IntlkAvailable if device is ready except for interlocks. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_IntlkTripInh | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Inhibit reporting of Sts_IntlkTrip and interlock trip alarm. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_RdyReset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Related object, reset by this object, is ready to be reset. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_Hand | Input | BOOL | CmdSrc.Inp_Hand | 0 | Decimal | 0 | 0 | 1 = Acquire Hand command source (typically hardwired local), 0 = Release Hand. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_Ovrd | Input | BOOL | CmdSrc.Inp_Ovrd | 0 | Decimal | 0 | 0 | 1 = Acquire Override command source (higher priority program logic), 0 = Release Override. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_OvrdCmd | Input | SINT |  | 0 | Decimal | 0 | 0 | Override device command: 0 = No command, 1 = State 0, 2 = State 1, 3 = State 2, 4 = State 3. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_ExtInh | Input | BOOL | CmdSrc.Inp_ExtInh | 0 | Decimal | 0 | 0 | 1 = Inhibit External command source acquisition, 0 = Allow External acquisition. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_HornInh | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Inhibit audible alert, 0 = Allow audible alert. | Read/Write | 0 | 0
raP_Dvc_D4SD | Inp_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset shed latches and cleared alarms. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_AllowDisable | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Maintenance to disable alarms. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_AllowShelve | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Operator to shelve alarms. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_NumStates | Input | SINT |  | 2 | Decimal | 0 | 0 | Number of device states. Valid = 2 to 4. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_bSt0OutWrite | Input | SINT |  | 2#0000_1111 | Binary | 0 | 0 | Bitmask, bits .0 - .3: If bit = 1, overwrite that output in State 0. If bit = 0, do not write that output in State 0. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_bSt0OutState | Input | SINT |  | 2#0000_0001 | Binary | 0 | 0 | Bitmask, bits .0 - .3: When written, if bit = 1, write 1 to that output in State 0. If bit = 0, write 0 to that output in State 0. | Read/Write | 0 | 0 | These configuration parameters determine how the outputs are used to command state. The parameter Cfg_bOutSt[x]Write configures which outputs get written for each state. The parameter Cfg_bOutSt[x]State configures what gets written for each state. For example, if all outputs must be set to 0 except Out_AData which must be set to 1 to command the device to state 1, then Cfg_bOutSt1Write must be 2#0000_1111 and Cfg_bOutSt1State must be 2#0000_0001. By default, all four outputs are written in every state, with a single output set to 1 in each state.
raP_Dvc_D4SD | Cfg_bSt1OutWrite | Input | SINT |  | 2#0000_1111 | Binary | 0 | 0 | Bitmask, bits .0 - .3: If bit = 1, overwrite that output in State 1. If bit = 0, do not write that output in State 1. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_bSt1OutState | Input | SINT |  | 2#0000_0010 | Binary | 0 | 0 | Bitmask, bits .0 - .3: When written, if bit = 1, write 1 to that output in State 1. If bit = 0, write 0 to that output in State 1. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_bSt2OutWrite | Input | SINT |  | 2#0000_1111 | Binary | 0 | 0 | Bitmask, bits .0 - .3: If bit = 1, overwrite that output in State 2. If bit = 0, do not write that output in State 2. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_bSt2OutState | Input | SINT |  | 2#0000_0100 | Binary | 0 | 0 | Bitmask, bits .0 - .3: When written, if bit = 1, write 1 to that output in State 2. If bit = 0, write 0 to that output in State 2. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_bSt3OutWrite | Input | SINT |  | 2#0000_1111 | Binary | 0 | 0 | Bitmask, bits .0 - .3: If bit = 1, overwrite that output in State 3. If bit = 0, do not write that output in State 3. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_bSt3OutState | Input | SINT |  | 2#0000_1000 | Binary | 0 | 0 | Bitmask, bits .0 - .3: When written, if bit = 1, write 1 to that output in State 3. If bit = 0, write 0 to that output in State 3. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_bSt0FdbkCheck | Input | SINT |  | 2#0000_0000 | Binary | 0 | 0 | Bitmask, bits .0 - .3: If bit = 1, check that feedback bit to verify State 0. If bit = 0, don't check that feedback bit (don't care). | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_bSt0FdbkState | Input | SINT |  | 2#0000_0001 | Binary | 0 | 0 | Bitmask, bits .0 - .3: If checking, if bit = 1, that feedback input is 1 in State 0. If bit = 0, that feedback input is 0 in State 0. | Read/Write | 0 | 0 | These configuration parameters determine how the inputs are used to determine state. The parameter Cfg_bSt[x]FdbkCheck configures which inputs get checked for each state. The parameter Cfg_bSt[x]FdbkState configures the values of the inputs which determine each state. For example, if the device returns a 0 to Inp_FdbkAData and Inp_FdbkBData and a 1 to Inp_FdbkCData when the device is in state 3, then Cfg_bSt3FdbkCheck must be 2#0000_0111 and Cfg_bSt2FdbkSt1State must be 2#0000_0100. By default, all inputs are ‘don’t’ care’ in every state (no feedback checking).
raP_Dvc_D4SD | Cfg_bSt1FdbkCheck | Input | SINT |  | 2#0000_0000 | Binary | 0 | 0 | Bitmask, bits .0 - .3: If bit = 1, check that feedback bit to verify State 1. If bit = 0, don't check that feedback bit (don't care). | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_bSt1FdbkState | Input | SINT |  | 2#0000_0010 | Binary | 0 | 0 | Bitmask, bits .0 - .3: If checking, if bit = 1, that feedback input is 1 in State 1. If bit = 0, that feedback input is 0 in State 1. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_bSt2FdbkCheck | Input | SINT |  | 2#0000_0000 | Binary | 0 | 0 | Bitmask, bits .0 - .3: If bit = 1, check that feedback bit to verify State 2. If bit = 0, don't check that feedback bit (don't care). | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_bSt2FdbkState | Input | SINT |  | 2#0000_0100 | Binary | 0 | 0 | Bitmask, bits .0 - .3: If checking, if bit = 1, that feedback input is 1 in State 2. If bit = 0, that feedback input is 0 in State 2. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_bSt3FdbkCheck | Input | SINT |  | 2#0000_0000 | Binary | 0 | 0 | Bitmask, bits .0 - .3: If bit = 1, check that feedback bit to verify State 3. If bit = 0, don't check that feedback bit (don't care). | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_bSt3FdbkState | Input | SINT |  | 2#0000_1000 | Binary | 0 | 0 | Bitmask, bits .0 - .3: If checking, if bit = 1, that feedback input is 1 in State 3. If bit = 0, that feedback input is 0 in State 3. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_St0onShed | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Go to State 0 on interlock or shed, 0 = Hold position on interlock or shed. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_Has0PermObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object is connected to Inp_St0Perm inputs, enable navigation. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_Has1PermObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object is connected to Inp_St1Perm inputs, enable navigation. | Read/Write | 0 | 0 | 1 = Tells HMI a permissive object (for example, PPERM) is used for Inp_PermOK0....3 and navigation to the channel object’s faceplate is enabled. IMPORTANT: The name of the Permissives object in the controller must be this object's name with the suffix ‘_Perm#’, where ‘#’ is the permissive number (0…3) For example, if your raP_Dvc_D4SD object has the name ’D4SD123’, then its Permissives object must be named‘D4SD123_Perm0’.
raP_Dvc_D4SD | Cfg_Has2PermObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object is connected to Inp_St2Perm inputs, enable navigation. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_Has3PermObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object is connected to Inp_St3Perm inputs, enable navigation. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_HasIntlkObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object is connected to Inp_Intlk inputs, enable navigation. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_HasMoreObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with more information is available, enable navigation. | Read/Write | 0 | 0 | 1 = Tells HMI an interlock object (for example, PINTLK) is used for Inp_IntlkOK and navigation to the interlock object’s faceplate is enabled. IMPORTANT: The name of the interlock object in the controller must be this object's name with the suffix '_Intlk'. For example, if your raP_Dvc_D4SD object has the name 'D4SD123', then its interlock object must be named 'D4SD123_Intlk'.
raP_Dvc_D4SD | Cfg_OperSt0Prio | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = OCmd_St0 is accepted any time, 0 = OCmd_St0 is accepted only when Operator command source is selected. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_ExtSt0Prio | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = XCmd_St0 is accepted any time, 0 = XCmd_St0 is accepted only when External command source is selected. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_OCmdResets | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A new Operator state command resets fault, 0 = A reset command is required to clear fault. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_XCmdResets | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A new External state command resets fault, 0 = A reset command is required to clear fault. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_OvrdPermIntlk | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Override ignores bypassable permissives and interlocks, 0 = Override uses all permissives and interlocks. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_ShedOnFail | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Go to State 0 and alarm on position fail, 0 = Alarm only. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_ShedOnIOFault | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Go to State 0 and alarm on I/O fault, 0 = Alarm only. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_ShedOnEqpFault | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Go to State 0 and alarm on equipment fault, 0 = Alarm only. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_HornOnChange | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Sound horn on any state change, 0 = Sound horn only on leaving State 0. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_HasOper | Input | BOOL | CmdSrc.Cfg_HasOper | 1 | Decimal | 0 | 0 | 1 = Operator (unlocked) command source exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_HasOperLocked | Input | BOOL | CmdSrc.Cfg_HasOperLocked | 1 | Decimal | 0 | 0 | 1 = Operator Locked command source exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_HasProg | Input | BOOL | CmdSrc.Cfg_HasProg | 1 | Decimal | 0 | 0 | 1 = Program (unlocked) command source exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_HasProgLocked | Input | BOOL | CmdSrc.Cfg_HasProgLocked | 1 | Decimal | 0 | 0 | 1 = Program Locked command source exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_HasExt | Input | BOOL | CmdSrc.Cfg_HasExt | 0 | Decimal | 0 | 0 | 1 = External command source exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_HasMaint | Input | BOOL | CmdSrc.Cfg_HasMaint | 1 | Decimal | 0 | 0 | 1 = Maintenance command source exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_HasMaintOoS | Input | BOOL | CmdSrc.Cfg_HasMaintOoS | 1 | Decimal | 0 | 0 | 1 = Maintenance Out of Service exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_OvrdOverLock | Input | BOOL | CmdSrc.Cfg_OvrdOverLock | 1 | Decimal | 0 | 0 | 1 = Override supersedes Program/Operator Locked, 0 = Don't supersede Program/Operator Locked. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_ExtOverLock | Input | BOOL | CmdSrc.Cfg_ExtOverLock | 0 | Decimal | 0 | 0 | 1 = External supersedes Program/Operator Locked, 0 = Don't supersede Program/Operator Locked. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_ProgPwrUp | Input | BOOL | CmdSrc.Cfg_ProgPwrUp | 0 | Decimal | 0 | 0 | 1 = Power up to Program command source, 0 = Power up to Operator command source. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_ProgNormal | Input | BOOL | CmdSrc.Cfg_ProgNormal | 0 | Decimal | 0 | 0 | Normal command source: 1 = Program, 0 = Operator. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_PCmdPriority | Input | BOOL | CmdSrc.Cfg_PCmdPriority | 0 | Decimal | 0 | 0 | Command priority: 1 = Program commands win, 0 = Operator commands win. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_PCmdProgAsLevel | Input | BOOL | CmdSrc.Cfg_PCmdProgAsLevel | 0 | Decimal | 0 | 0 | 1 = Program/Operator selection follows PCmd_Prog as level (1 for Program, 0 for Operator), 0 = PCmd_Prog is used as edge to select Program, PCmd_Oper selects Operator. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_PCmdLockAsLevel | Input | BOOL | CmdSrc.Cfg_PCmdLockAsLevel | 0 | Decimal | 0 | 0 | 1 = Program lock selection follows PCmd_Lock as level (1 for locked, 0 for unlocked), 0 = PCmd_Lock is used as edge to select Program Locked, PCmd_Unlock selects Program (unlocked). | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_ExtAcqAsLevel | Input | BOOL | CmdSrc.Cfg_ExtAcqAsLevel | 0 | Decimal | 0 | 0 | 1 = External selection follows XCmd_Acq as level (1 to acquire External, 0 to release External), 0 = XCmd_Acq is used as edge to acquire External, XCmd_Rel is used to release External. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_OutAPulseTime | Input | REAL |  | 0 | Float | 0 | 0 | Time to pulse Out_AData (seconds). Valid = 0.0 to 2147483.0, 0.0 = Output held continuously. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_OutBPulseTime | Input | REAL |  | 0 | Float | 0 | 0 | Time to pulse Out_BData (seconds). Valid = 0.0 to 2147483.0, 0.0 = Output held continuously. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_OutCPulseTime | Input | REAL |  | 0 | Float | 0 | 0 | Time to pulse Out_CData (seconds). Valid = 0.0 to 2147483.0, 0.0 = Output held continuously. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_OutDPulseTime | Input | REAL |  | 0 | Float | 0 | 0 | Time to pulse Out_DData (seconds). Valid = 0.0 to 2147483.0, 0.0 = Output held continuously. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_StartHornTime | Input | REAL |  | 0 | Float | 0 | 0 | Time to sound audible on device state change (seconds). Valid = 0.0 to 1000.0, 0.0 = Disabled. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_VirtualFdbkTime | Input | REAL |  | 2 | Float | 0 | 0 | Time to simulate reaching target state when virtualized (seconds). Valid = 0.0 to 2147483.0. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_FailTime | Input | REAL |  | 10 | Float | 0 | 0 | Time to receive state feedback before declaring failure (seconds). Valid = 0.0 to 2147483.0. | Read/Write | 0 | 0
raP_Dvc_D4SD | Cfg_CnfrmReqd | Input | SINT |  | 0 | Decimal | 0 | 0 | Operator command confirmation or e-signature type required: 0 = None, 1 = Command confirmation required, 2 = Performer e-signature required, 3 = Performer and approver e-signature required. | Read/Write | 0 | 0
raP_Dvc_D4SD | PSet_Owner | Input | DINT |  | 0 | Decimal | 0 | 0 | Program ownership request: Non-zero Owner ID = Acquire, 0 = Release. | Read/Write | 0 | 0
raP_Dvc_D4SD | PCmd_Virtual | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program Command to select Virtual (simulated) device operation. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | PCmd_Physical | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program Command to select Physical device operation (not simulated). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | PCmd_St0 | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program Command to set device to State 0. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | PCmd_St1 | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program Command to set device to State 1. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | PCmd_St2 | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program Command to set device to State 2. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | PCmd_St3 | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program Command to set device to State 3. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | PCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program Command to reset shed latches and returned-to-normal latched alarms. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | PCmd_Prog | Input | BOOL | CmdSrc.PCmd_Prog | 0 | Decimal | 0 | 0 | Program Command to select Program command source. The instruction clears this operand automatically if Cfg_PCmdProgAsLevel = 0. | Read/Write | 0 | 0
raP_Dvc_D4SD | PCmd_Oper | Input | BOOL | CmdSrc.PCmd_Oper | 0 | Decimal | 0 | 0 | Program Command to select Operator command source. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | PCmd_Lock | Input | BOOL | CmdSrc.PCmd_Lock | 0 | Decimal | 0 | 0 | Program Command to lock Program command source and disallow Operator. The instruction clears this operand automatically if Cfg_PCmdLockAsLevel = 0. | Read/Write | 0 | 0
raP_Dvc_D4SD | PCmd_Unlock | Input | BOOL | CmdSrc.PCmd_Unlock | 0 | Decimal | 0 | 0 | Program Command to unlock Program command source and allow Operator to acquire. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | PCmd_Normal | Input | BOOL | CmdSrc.PCmd_Normal | 0 | Decimal | 0 | 0 | Program Command to select normal command source (Operator or Program). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | XCmd_St0 | Input | BOOL |  | 0 | Decimal | 0 | 0 | External Command to set device to State 0. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | XCmd_St1 | Input | BOOL |  | 0 | Decimal | 0 | 0 | External Command to set device to State 1. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | XCmd_St2 | Input | BOOL |  | 0 | Decimal | 0 | 0 | External Command to set device to State 2. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | XCmd_St3 | Input | BOOL |  | 0 | Decimal | 0 | 0 | External Command to set device to State 3. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | XCmd_Acq | Input | BOOL | CmdSrc.XCmd_Acq | 0 | Decimal | 0 | 0 | External Command to acquire command source. The instruction clears this operand automatically if Cfg_ExtAcqAsLevel = 0. | Read/Write | 0 | 0
raP_Dvc_D4SD | XCmd_Rel | Input | BOOL | CmdSrc.XCmd_Rel | 0 | Decimal | 0 | 0 | External Command to release command source, accepted if Cfg_ExtAcqAsLevel = 0. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | XCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | External Command to reset shed latches and returned-to-normal latched alarms. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_D4SD | XCmd_ResetAckAll | Input | BOOL |  | 0 | Decimal | 0 | 0 | External Command to acknowledge all alarms and reset latched alarms and shed conditions. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_nPos | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Ladder Diagram: If the rung-in condition is true, the instruction’s Logic routine executes. If the rung- in condition is false, the instruction’s EnableInFalse routine executes. Function Block Diagram: If true, or not connected, the instruction’s Logic routine executes. If the parameter is exposed as a pin and wired, and the pin is false, the instruction’s EnableInFalse routine executes. Structured Text: No effect. The instruction’s Logic routine executes. | Read Only | 0
raP_Dvc_nPos | Inp_InitializeReq | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Request to initialize the instruction. The instruction is normally initialized in instruction first run. Use this request when reinitialization is needed. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_OwnerCmd | Input | DINT |  | 0 | Decimal | 0 | 0 | Owner device command. 0 = None, .10 = Operator lock, .11 = Operator unlock, .12 = Program lock, .13 = Program unlock, .14 = Acquire maintenance, .15 = Release maintenance, .16 = Acquire external, .17 = Release external, .29 = Echo. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos01FdbkData | Input | BOOL | Wrk_bInp.1 | 0 | Decimal | 0 | 1 | Position 1 feedback, 1 = Device is confirmed at Position 1. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos02FdbkData | Input | BOOL | Wrk_bInp.2 | 0 | Decimal | 0 | 1 | Position 2 feedback, 1 = Device is confirmed at Position 2. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos03FdbkData | Input | BOOL | Wrk_bInp.3 | 0 | Decimal | 0 | 1 | Position 3 feedback, 1 = Device is confirmed at Position 3. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos04FdbkData | Input | BOOL | Wrk_bInp.4 | 0 | Decimal | 0 | 1 | Position 4 feedback, 1 = Device is confirmed at Position 4. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos05FdbkData | Input | BOOL | Wrk_bInp.5 | 0 | Decimal | 0 | 1 | Position 5 feedback, 1 = Device is confirmed at Position 5. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos06FdbkData | Input | BOOL | Wrk_bInp.6 | 0 | Decimal | 0 | 1 | Position 6 feedback, 1 = Device is confirmed at Position 6. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos07FdbkData | Input | BOOL | Wrk_bInp.7 | 0 | Decimal | 0 | 1 | Position 7 feedback, 1 = Device is confirmed at Position 7. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos08FdbkData | Input | BOOL | Wrk_bInp.8 | 0 | Decimal | 0 | 1 | Position 8 feedback, 1 = Device is confirmed at Position 8. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos09FdbkData | Input | BOOL | Wrk_bInp.9 | 0 | Decimal | 0 | 0 | Position 9 feedback, 1 = Device is confirmed at Position 9. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos10FdbkData | Input | BOOL | Wrk_bInp.10 | 0 | Decimal | 0 | 0 | Position 10 feedback, 1 = Device is confirmed at Position 10. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos11FdbkData | Input | BOOL | Wrk_bInp.11 | 0 | Decimal | 0 | 0 | Position 11 feedback, 1 = Device is confirmed at Position 11. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos12FdbkData | Input | BOOL | Wrk_bInp.12 | 0 | Decimal | 0 | 0 | Position 12 feedback, 1 = Device is confirmed at Position 12. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos13FdbkData | Input | BOOL | Wrk_bInp.13 | 0 | Decimal | 0 | 0 | Position 13 feedback, 1 = Device is confirmed at Position 13. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos14FdbkData | Input | BOOL | Wrk_bInp.14 | 0 | Decimal | 0 | 0 | Position 14 feedback, 1 = Device is confirmed at Position 14. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos15FdbkData | Input | BOOL | Wrk_bInp.15 | 0 | Decimal | 0 | 0 | Position 15 feedback, 1 = Device is confirmed at Position 15. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos16FdbkData | Input | BOOL | Wrk_bInp.16 | 0 | Decimal | 0 | 0 | Position 16 feedback, 1 = Device is confirmed at Position 16. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos17FdbkData | Input | BOOL | Wrk_bInp.17 | 0 | Decimal | 0 | 0 | Position 17 feedback, 1 = Device is confirmed at Position 17. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos18FdbkData | Input | BOOL | Wrk_bInp.18 | 0 | Decimal | 0 | 0 | Position 18 feedback, 1 = Device is confirmed at Position 18. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos19FdbkData | Input | BOOL | Wrk_bInp.19 | 0 | Decimal | 0 | 0 | Position 19 feedback, 1 = Device is confirmed at Position 19. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos20FdbkData | Input | BOOL | Wrk_bInp.20 | 0 | Decimal | 0 | 0 | Position 20 feedback, 1 = Device is confirmed at Position 20. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos21FdbkData | Input | BOOL | Wrk_bInp.21 | 0 | Decimal | 0 | 0 | Position 21 feedback, 1 = Device is confirmed at Position 21. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos22FdbkData | Input | BOOL | Wrk_bInp.22 | 0 | Decimal | 0 | 0 | Position 22 feedback, 1 = Device is confirmed at Position 22. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos23FdbkData | Input | BOOL | Wrk_bInp.23 | 0 | Decimal | 0 | 0 | Position 23 feedback, 1 = Device is confirmed at Position 23. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos24FdbkData | Input | BOOL | Wrk_bInp.24 | 0 | Decimal | 0 | 0 | Position 24 feedback, 1 = Device is confirmed at Position 24. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos25FdbkData | Input | BOOL | Wrk_bInp.25 | 0 | Decimal | 0 | 0 | Position 25 feedback, 1 = Device is confirmed at Position 25. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos26FdbkData | Input | BOOL | Wrk_bInp.26 | 0 | Decimal | 0 | 0 | Position 26 feedback, 1 = Device is confirmed at Position 26. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos27FdbkData | Input | BOOL | Wrk_bInp.27 | 0 | Decimal | 0 | 0 | Position 27 feedback, 1 = Device is confirmed at Position 27. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos28FdbkData | Input | BOOL | Wrk_bInp.28 | 0 | Decimal | 0 | 0 | Position 28 feedback, 1 = Device is confirmed at Position 28. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos29FdbkData | Input | BOOL | Wrk_bInp.29 | 0 | Decimal | 0 | 0 | Position 29 feedback, 1 = Device is confirmed at Position 29. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Pos30FdbkData | Input | BOOL | Wrk_bInp.30 | 0 | Decimal | 0 | 0 | Position 30 feedback, 1 = Device is confirmed at Position 30. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_LockFdbkData | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is confirmed locked / sealed in position. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_UnlockFdbkData | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is confirmed unlocked / unsealed and is free to move. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_CylExtFdbkData | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device indexing cylinder is confirmed extended. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_CylRetrFdbkData | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device indexing cylinder is confirmed retracted. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_CylLeftFdbkData | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device indexing cylinder is confirmed in left (increasing) position. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_CylRightFdbkData | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device indexing cylinder is confirmed in right (decreasing) position. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_IOFault | Input | BOOL |  | 0 | Decimal | 0 | 1 | Indicates the I/O communication is faulted. 0 = The I/O data are good, 1 = The I/O data are bad, causing fault. If the Valve is not virtual, this input sets Sts_IOFault, which raises I/OFault Alarm. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_PermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Permissives are OK, device can energize. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_NBPermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Non-Bypassable Permissives are OK, device can energize. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_IntlkOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Interlocks OK, device can energize, 0 = not OK, device must de-energize or drive to position 1. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_NBIntlkOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Non-Bypassable Interlocks OK, device can energize, 0 = not OK, device must de-energize or drive to position 1. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_IntlkAvailable | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Interlock Availibility OK. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_IntlkTripInh | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Inhibit Interlock Trip Status. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_RdyReset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Related object, reset by this object, is ready to be reset. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Hand | Input | BOOL | CmdSrc.Inp_Hand | 0 | Decimal | 0 | 0 | 1 = Acquire Hand (typically hardwired local), 0 = Release Hand. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Ovrd | Input | BOOL | CmdSrc.Inp_Ovrd | 0 | Decimal | 0 | 0 | 1 = Acquire Override (higher priority program logic), 0 = Release Override. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_OvrdCmd | Input | DINT |  | 0 | Decimal | 0 | 0 | Override Command 0 = None, 1 = Position 1, 2 = Position 2, ..., 30 = Position 30. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_ExtInh | Input | BOOL | CmdSrc.Inp_ExtInh | 0 | Decimal | 0 | 0 | 1 = Inhibit External acquisition, 0 = Allow External acquisition. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_HornInh | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Inhibit audible alert, 0 = Alllow audible alert. | Read/Write | 0 | 0
raP_Dvc_nPos | Inp_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset shed latches and cleared alarms. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_AllowDisable | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Maintenance to disable alarms. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_AllowShelve | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Operator to shelve alarms. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_NumPos | Input | DINT |  | 3 | Decimal | 0 | 0 | Number of device positions, valid = 2 to 30. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_Circ | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Positions are circular (rotary device, after position n is position 1), 0 = linear device (positions 1 and n are at ends of travel). | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_CWOnly | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Circular (rotary) device can only rotate "clockwise", 0 = circular device is bidirectional, use shortest path. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_ViaPos1 | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Drive linear device to position 1 on every move, 0 = move direct to set position. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_IntlkToPos1 | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Drive to position 1 on interlock or fault, 0 = De-energize only on interlock or fault. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_OutPosLatch | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Latch in Out_PosXXData until a new position is set, 0 = clear output upon reaching set position. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_HasLock | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device has a lock or seal, must unlock / unseal before moving. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_HasPosFdbk | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device has position feedback for all positions. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_UsePosFdbk | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Use position feedback to check device reached set position. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_HasLockFdbk | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device has locked / unlocked feedback. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_UseLockFdbk | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Use lock feedback to verify locking and unlocking of device. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_HasCylFdbk | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device indexing cylinders have position feedback. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_UseCylFdbk | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Use Indexing cylinder position feedback to verify cylinder motion. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_HasPermObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI a permissive object (for example, PPERM) is used for PermOK inputs and navigation to the permissive object’s faceplate is enabled. IMPORTANT: The name of the Permissives object in the controller must be this object's name with the suffix ‘_Perm’. For example, if your raP_Dvc_nPos object has the name ’nPos123’, then its Permissives object must be named‘nPos123_Perm’. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_HasIntlkObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an interlock object (for example, PINTLK) is used for IntlkOK inputs and navigation to the interlock object’s faceplate is enabled. IMPORTANT: The name of the interlock object in the controller must be this object's name with the suffix '_Intlk'. For example, if your raP_Dvc_nPos object has the name 'nPos123', then its interlock object must be named 'nPos123_Intlk'. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_HasMoreObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with more information is available. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_OperPos01Prio | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = OSet_Pos setting = 1 accepted any time; 0 = OSet_Pos accepted only when Oper is selected. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_ExtPos01Prio | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = XSet_Pos setting = 1 accepted any time; 0 = XCmd_Pos accepted only when Ext is selected. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_OSetResets | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = New Operator position setting resets fault, 0 = Reset required to clear fault. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_XSetResets | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = New External position setting resets fault, 0 = Reset required to clear fault. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_SetDuringMove | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = New position setting received during move is accepted, 0 = must wait for previous move to complete. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_OvrdPermIntlk | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Override ignores bypassable permissives/interlocks, 0 = Always use permissives/interlocks. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_ShedOnPosFail | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = De-energize device or go to position 1 and Alarm on Position Fail, 0 = Alarm only. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_ShedOnLockFail | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = De-energize device or go to position 1 and Alarm on Lock Fail, 0 = Alarm only. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_ShedOnIOFault | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = De-energize device or go to position 1 and Alarm on I/O Fault, 0 = Alarm only. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_HornOnChange | Input | BOOL |  | 0 | Decimal | 0 | 0 | 0 = Horn on leaving position 1 only, 1 = Horn on any position change. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_HasOper | Input | BOOL | CmdSrc.Cfg_HasOper | 1 | Decimal | 0 | 0 | 1 = Operator (unlocked) exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_HasOperLocked | Input | BOOL | CmdSrc.Cfg_HasOperLocked | 1 | Decimal | 0 | 0 | 1 = Operator locked exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_HasProg | Input | BOOL | CmdSrc.Cfg_HasProg | 1 | Decimal | 0 | 0 | 1 = Program (unlocked) exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_HasProgLocked | Input | BOOL | CmdSrc.Cfg_HasProgLocked | 1 | Decimal | 0 | 0 | 1 = Program locked exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_HasExt | Input | BOOL | CmdSrc.Cfg_HasExt | 0 | Decimal | 0 | 0 | 1 = External exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_HasMaint | Input | BOOL | CmdSrc.Cfg_HasMaint | 1 | Decimal | 0 | 0 | 1 = Maintenance exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_HasMaintOoS | Input | BOOL | CmdSrc.Cfg_HasMaintOoS | 1 | Decimal | 0 | 0 | 1 = Maintenance Out of Service exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_OvrdOverLock | Input | BOOL | CmdSrc.Cfg_OvrdOverLock | 1 | Decimal | 0 | 0 | 1 = Override supersedes Program/Operator lock, 0 = Don't Override lock. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_ExtOverLock | Input | BOOL | CmdSrc.Cfg_ExtOverLock | 0 | Decimal | 0 | 0 | 1 = External supersedes Program/Operator lock, 0 = Don't Override lock. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_ProgPwrUp | Input | BOOL | CmdSrc.Cfg_ProgPwrUp | 0 | Decimal | 0 | 0 | 1 = Power up to Program, 0 = Power up to Operator. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_ProgNormal | Input | BOOL | CmdSrc.Cfg_ProgNormal | 0 | Decimal | 0 | 0 | Normal source: 1 = Program if no requests; 0 = Operator if no requests. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_PCmdPriority | Input | BOOL | CmdSrc.Cfg_PCmdPriority | 0 | Decimal | 0 | 0 | Command priority. 1 = Program commands win, 0 = Operator commands win. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_PCmdProgAsLevel | Input | BOOL | CmdSrc.Cfg_PCmdProgAsLevel | 0 | Decimal | 0 | 0 | 1 = PCmd_Prog used as a level (1 = Prog, 0 = Oper). | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_PCmdLockAsLevel | Input | BOOL | CmdSrc.Cfg_PCmdLockAsLevel | 0 | Decimal | 0 | 0 | 1 = PCmd_Lock used as a level (1 = Lock, 0 = Unlock). | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_ExtAcqAsLevel | Input | BOOL | CmdSrc.Cfg_ExtAcqAsLevel | 0 | Decimal | 0 | 0 | 1 = XCmd_Acq used as level (1 = Acquire, 0 = Release). | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_Retries | Input | SINT |  | 3 | Decimal | 0 | 0 | Number of retries via position 1 before declaring failure, 0 = don't retry, valid = 0 to 3. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_ExtendDelay | Input | REAL |  | 0 | Float | 0 | 0 | Delay before extending cylinder to engage for move, valid = 0.0 to 2147483.0 seconds. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_VerifyDelay | Input | REAL |  | 1 | Float | 0 | 0 | Delay to verify device has settled in commanded position, valid = 0.0 to 2147483.0 seconds. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_PosCheckTime | Input | REAL |  | 30 | Float | 0 | 0 | Time to receive position feedback before declaring failure, valid = 0.0 to 2147483.0 seconds. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_LockCheckTime | Input | REAL |  | 5 | Float | 0 | 0 | Time to receive locked / unlocked feedback before declaring lock failure, valid = 0.0 to 2147483.0 seconds. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_VirtualPosTime | Input | REAL |  | 1 | Float | 0 | 0 | Time to simulate reaching target position when virtualized, valid = 0.0 to 2147483.0 seconds. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_VirtualLockTime | Input | REAL |  | 1 | Float | 0 | 0 | Time to simulate lock or unlock when virtualized, valid = 0.0 to 2147483.0 seconds. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_VirtualCylTime | Input | REAL |  | 0.5 | Float | 0 | 0 | Time to simulate index cylinder feedback when virtualized, valid = 0.0 to 21474830 seconds. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_StartHornTime | Input | REAL |  | 0 | Float | 0 | 0 | Time in seconds to sound audible on device position change, valid = 0.0 to 1000.0 seconds, 0.0 = disabled. | Read/Write | 0 | 0
raP_Dvc_nPos | Cfg_CnfrmReqd | Input | SINT |  | 0 | Decimal | 0 | 0 | Operator Command Confirmation Required. Represents the type of command confirmation required. 0 = None, 1 = Command confirmation required, 2 = Performer e-signature required, 3 = Performer and approver e-signature required. | Read/Write | 0 | 0
raP_Dvc_nPos | PSet_Owner | Input | DINT |  | 0 | Decimal | 0 | 0 | Program Owner Request ID (non-zero) or Release (zero). | Read/Write | 0 | 0
raP_Dvc_nPos | PSet_Pos | Input | SINT |  | 0 | Decimal | 0 | 0 | Program Setting: commanded position 1 to 30, 0 = no change. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_nPos | PCmd_Virtual | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to select Virtual (simulated) device operation. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_nPos | PCmd_Physical | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to select Physical device operation (not simulated). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_nPos | PCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to reset all alarms requiring reset. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_nPos | PCmd_Prog | Input | BOOL | CmdSrc.PCmd_Prog | 0 | Decimal | 0 | 0 | Program command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_nPos | PCmd_Oper | Input | BOOL | CmdSrc.PCmd_Oper | 0 | Decimal | 0 | 0 | Program command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_nPos | PCmd_Lock | Input | BOOL | CmdSrc.PCmd_Lock | 0 | Decimal | 0 | 0 | Program command to lock Program (disallow Operator). The instruction clears this operand automatically if Cfg_PCmdLockAsLevel = 0. | Read/Write | 0 | 0
raP_Dvc_nPos | PCmd_Unlock | Input | BOOL | CmdSrc.PCmd_Unlock | 0 | Decimal | 0 | 0 | Program command to unlock Program (allow Operator to acquire). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_nPos | PCmd_Normal | Input | BOOL | CmdSrc.PCmd_Normal | 0 | Decimal | 0 | 0 | Program command to select normal command source (Operator or Program). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_nPos | XSet_Pos | Input | SINT |  | 0 | Decimal | 0 | 0 | External Setting: commanded position 1 to 30, 0 = no change. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_nPos | XCmd_Acq | Input | BOOL | CmdSrc.XCmd_Acq | 0 | Decimal | 0 | 0 | External command to acquire ownership (Operator/Program/Override/Maintenance to External). The instruction clears this operand automatically if Cfg_ExtAcqAsLevel = 0. | Read/Write | 0 | 0
raP_Dvc_nPos | XCmd_Rel | Input | BOOL | CmdSrc.XCmd_Rel | 0 | Decimal | 0 | 0 | External command to release ownership if Cfg_ExtAcqAsLevel = 0 (External to Operator/Program/Override/Maintenance). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_nPos | XCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to clear shed latches and cleared alarms. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_nPos | XCmd_ResetAckAll | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to acknowledge and reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Ladder Diagram: If the rung-in condition is true, the instruction’s Logic routine executes. If the rung- in condition is false, the instruction’s EnableInFalse routine executes. Function Block Diagram: If true, or not connected, the instruction’s Logic routine executes. If the parameter is exposed as a pin and wired, and the pin is false, the instruction’s EnableInFalse routine executes. Structured Text: No effect. The instruction’s Logic routine executes. | Read Only | 0
raP_Dvc_VlvMP | Inp_InitializeReq | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Request to initialize the instruction. The instruction is normally initialized in instruction first run. Use this request when reinitialization is needed. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_OwnerCmd | Input | DINT |  | 0 | Decimal | 0 | 0 | Owner device command. 0 = None, .10 = Operator lock, .11 = Operator unlock, .12 = Program lock, .13 = Program unlock, .14 = Acquire maintenance, .15 = Release maintenance, .16 = Acquire external, .17 = Release external, .29 = Echo. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_OpenLSData | Input | BOOL |  | 0 | Decimal | 0 | 1 | Valve Open Limit Switch, 1 = confirmed open. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_ClosedLSData | Input | BOOL |  | 0 | Decimal | 0 | 1 | Valve Closed Limit Switch, 1 = confirmed closed. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_LowerSeatLSData | Input | BOOL |  | 0 | Decimal | 0 | 1 | Valve Lower Seat Lift Limit Switch, 1 = confirmed lower seat lifted. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_UpperSeatLSData | Input | BOOL |  | 0 | Decimal | 0 | 1 | Valve Upper Seat Lift Limit Switch, 1 = confirmed upper seat lifted. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_CavityInletLSData | Input | BOOL |  | 0 | Decimal | 0 | 1 | Valve Cavity Inlet Valve Limit Switch, 1 = confirmed cavity inlet open. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_CavityOutletLSData | Input | BOOL |  | 0 | Decimal | 0 | 1 | Valve Cavity Outlet Valve Limit Switch, 1 = confirmed cavity output closed. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_IOFault | Input | BOOL |  | 0 | Decimal | 0 | 1 | Indicates the I/O communication is faulted. 0 = The I/O data are good, 1 = The I/O data are bad, causing fault. If the Valve is not virtual, this input sets Sts_IOFault, which raises I/OFault Alarm. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_PermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Permissives OK, valve can energize. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_NBPermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Non-Bypassable Permissives OK, valve can energize. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_IntlkOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Interlocks OK, valve can energize, 0 = not OK, valve must de-energize. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_NBIntlkOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Non-Bypassable Interlocks OK, valve can energize, 0 = not OK, valve must de-energize. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_IntlkAvailable | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Interlock Availibility OK. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_IntlkTripInh | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Inhibit Interlock Trip Status. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_RdyReset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Related object, reset by this object, is ready to be reset. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_Hand | Input | BOOL | CmdSrc.Inp_Hand | 0 | Decimal | 0 | 0 | 1 = Acquire Hand (typically hardwired local), 0 = Release Hand. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_Ovrd | Input | BOOL | CmdSrc.Inp_Ovrd | 0 | Decimal | 0 | 0 | 1 = Acquire Override (higher priority program logic), 0 = Release Override. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_OvrdCmd | Input | SINT |  | 0 | Decimal | 0 | 0 | Override Command 0 = None, 1 = Close, 2 = Open, 3 = Lift lower seat, 4 = Lift upper seat, 5 = Clean cavity, 6 = Clean lower seat, 7 = Clean upper seat. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_ExtInh | Input | BOOL | CmdSrc.Inp_ExtInh | 0 | Decimal | 0 | 0 | 1 = Inhibit External acquisition, 0 = Allow External acquisition. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_HornInh | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Inhibit audible alert, 0 = Alllow audible alert. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Inp_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset shed latches and cleared alarms. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_AllowDisable | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Maintenance to disable alarms. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_AllowShelve | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Operator to shelve alarms. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_HasLiftLower | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Valve supports Lift Lower Seat state. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_HasLiftUpper | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Valve supports Lift Upper Seat state. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_HasCleanCavity | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Valve supports Clean Cavity state. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_HasCleanLower | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Valve supports Clean Lower Seat state. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_HasCleanUpper | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Valve supports Clean Upper Seat state. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_PulseLiftLower | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Pulse seat lift output when lifting Lower seat. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_PulseLiftUpper | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Pulse seat lift output when lifting Upper seat. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_PulseCleanLower | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Pulse seat lift output when cleaning Lower seat. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_PulseCleanUpper | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Pulse seat lift output when cleaning Upper seat. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_HasPermObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI a permissive object (for example, PPERM) is used for Inp_PermOK and navigation to the permissive object’s faceplate is enabled. IMPORTANT: The name of the Permissive object in the controller must be this object's name with the suffix ‘_Perm’. For example, if your raP_Dvc_VlvMP object has the name ’ValveMP123’, then its Permissive object must be named ‘ValveMP123_Perm’. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_HasIntlkObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an interlock object (for example, PINTLK) is used for Inp_IntlkOK and navigation to the interlock object’s faceplate is enabled. IMPORTANT: The name of the interlock object in the controller must be this object's name with the suffix ‘_Intlk’. For example, if your raP_Dvc_VlvMP object has the name ’ValveMP123’, then its interlock object must be named ‘ValveMP123_Intlk’. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_HasStatsObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI a valve statistics object (for example, PVLVS) is used and navigation to the valve statistics object’s faceplate is enabled. IMPORTANT: The name of the Valve Statistics object in the controller must be this object's name with the suffix‘_ValveStats. For example, if your raP_Dvc_VlvMP object has the name ’ValveMP123’, then its Interlock object must be named ‘ValveMP123_ValveStats’. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_HasMoreObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with more information is available. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_OperClosePrio | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = OCmd_Close accepted any time; 0 = OCmd_Close accepted only when Oper is selected. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_ExtClosePrio | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = XCmd_Close accepted any time; 0 = XCmd_Close accepted only when Ext is selected. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_OCmdResets | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = New Operator state command resets fault, 0 = Reset required to clear fault. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_XCmdResets | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = New External state command resets fault, 0 = Reset required to clear fault. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_OvrdPermIntlk | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Override ignores bypassable permissives/interlocks, 0 = Always use permissives/interlocks. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_ShedOnFail | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Close valve and alarm on Position Fail. 0 = Alarm only on Fail. IMPORTANT: If a condition is configured to shed the device to the Off state on a fault, a reset is required to clear the shed fault to command the device to a state other than closed. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_ShedOnIOFault | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Close Valve and Alarm on I/O Fault. 0 = Alarm only on I/O Fault. IMPORTANT: If a condition is configured to shed the device to the Off state on a fault, a reset is required to clear the shed fault to command the device to a state other than closed. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_HasOper | Input | BOOL | CmdSrc.Cfg_HasOper | 1 | Decimal | 0 | 0 | 1 = Operator (unlocked) exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_HasOperLocked | Input | BOOL | CmdSrc.Cfg_HasOperLocked | 1 | Decimal | 0 | 0 | 1 = Operator locked exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_HasProg | Input | BOOL | CmdSrc.Cfg_HasProg | 1 | Decimal | 0 | 0 | 1 = Program (unlocked) exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_HasProgLocked | Input | BOOL | CmdSrc.Cfg_HasProgLocked | 1 | Decimal | 0 | 0 | 1 = Program locked exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_HasExt | Input | BOOL | CmdSrc.Cfg_HasExt | 0 | Decimal | 0 | 0 | 1 = External exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_HasMaint | Input | BOOL | CmdSrc.Cfg_HasMaint | 1 | Decimal | 0 | 0 | 1 = Maintenance exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_HasMaintOoS | Input | BOOL | CmdSrc.Cfg_HasMaintOoS | 1 | Decimal | 0 | 0 | 1 = Maintenance Out of Service exists, can be selected. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_OvrdOverLock | Input | BOOL | CmdSrc.Cfg_OvrdOverLock | 1 | Decimal | 0 | 0 | 1 = Override supersedes Program/Operator lock, 0 = Don't Override lock. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_ExtOverLock | Input | BOOL | CmdSrc.Cfg_ExtOverLock | 0 | Decimal | 0 | 0 | 1 = External supersedes Program/Operator lock, 0 = Don't Override lock. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_ProgPwrUp | Input | BOOL | CmdSrc.Cfg_ProgPwrUp | 0 | Decimal | 0 | 0 | 1 = Power up to Program, 0 = Power up to Operator. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_ProgNormal | Input | BOOL | CmdSrc.Cfg_ProgNormal | 0 | Decimal | 0 | 0 | Normal source: 1 = Program if no requests; 0 = Operator if no requests. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_PCmdPriority | Input | BOOL | CmdSrc.Cfg_PCmdPriority | 0 | Decimal | 0 | 0 | Command priority. 1 = Program commands win, 0 = Operator commands win. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_PCmdProgAsLevel | Input | BOOL | CmdSrc.Cfg_PCmdProgAsLevel | 0 | Decimal | 0 | 0 | 1 = PCmd_Prog used as a level (1 = Prog, 0 = Oper). | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_PCmdLockAsLevel | Input | BOOL | CmdSrc.Cfg_PCmdLockAsLevel | 0 | Decimal | 0 | 0 | 1 = PCmd_Lock used as a level (1 = Lock, 0 = Unlock). | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_ExtAcqAsLevel | Input | BOOL | CmdSrc.Cfg_ExtAcqAsLevel | 0 | Decimal | 0 | 0 | 1 = XCmd_Acq used as level (1 = Acquire, 0 = Release). | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_OpenPulseTime | Input | REAL |  | 10 | Float | 0 | 0 | Time to lift seat when pulsing for cleaning, valid = 0.0 to 2147483.0 seconds. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_ClosePulseTime | Input | REAL |  | 5 | Float | 0 | 0 | Time to close seat when pulsing for cleaning, valid = 0.0 to 2147483.0 seconds. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_StartHornTime | Input | REAL |  | 0 | Float | 0 | 0 | Time in seconds to sound audible on command to move from the closed position, valid = 0.0 to 1000.0 seconds, 0.0 = disabled. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_FailTime | Input | REAL |  | 3 | Float | 0 | 0 | Time after output to get position feedback before fault, valid = 0.0 to 2147483.0 seconds. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Cfg_CnfrmReqd | Input | SINT |  | 0 | Decimal | 0 | 0 | Operator Command Confirmation Required. Represents the type of command confirmation required. 0 = None, 1 = Command confirmation required, 2 = Performer e-signature required, 3 = Performer and approver e-signature required. | Read/Write | 0 | 0
raP_Dvc_VlvMP | PSet_Owner | Input | DINT |  | 0 | Decimal | 0 | 0 | Program Owner Request ID (non-zero) or Release (zero). | Read/Write | 0 | 0
raP_Dvc_VlvMP | PCmd_Virtual | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to select Virtual (simulated) device operation. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | PCmd_Physical | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to select Physical device operation (not simulated). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | PCmd_Close | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program Command to Close valve. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | PCmd_Open | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program Command to Open valve. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | PCmd_LiftLower | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to Lift lower seat. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | PCmd_LiftUpper | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to Lift upper seat. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | PCmd_CleanCavity | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to Clean valve leakage cavity. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | PCmd_CleanLower | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to Clean lower seat. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | PCmd_CleanUpper | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to Clean upper seat. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | PCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to reset all alarms requiring reset. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | PCmd_Prog | Input | BOOL | CmdSrc.PCmd_Prog | 0 | Decimal | 0 | 0 | Program command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | PCmd_Oper | Input | BOOL | CmdSrc.PCmd_Oper | 0 | Decimal | 0 | 0 | Program command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | PCmd_Lock | Input | BOOL | CmdSrc.PCmd_Lock | 0 | Decimal | 0 | 0 | Program command to lock Program (disallow Operator). The instruction clears this operand automatically if Cfg_PCmdLockAsLevel = 0. | Read/Write | 0 | 0
raP_Dvc_VlvMP | PCmd_Unlock | Input | BOOL | CmdSrc.PCmd_Unlock | 0 | Decimal | 0 | 0 | Program command to unlock Program (allow Operator to acquire). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | PCmd_Normal | Input | BOOL | CmdSrc.PCmd_Normal | 0 | Decimal | 0 | 0 | Program command to select normal command source (Operator or Program). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | XCmd_Close | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to Close valve. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | XCmd_Open | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to Open valve. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | XCmd_LiftLower | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to Lift lower seat. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | XCmd_LiftUpper | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to Lift upper seat. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | XCmd_CleanCavity | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to Clean valve leakage cavity. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | XCmd_CleanLower | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to Clean lower seat. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | XCmd_CleanUpper | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to Clean upper seat. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | XCmd_Acq | Input | BOOL | CmdSrc.XCmd_Acq | 0 | Decimal | 0 | 0 | External command to acquire ownership (Operator/Program/Override/Maintenance to External). The instruction clears this operand automatically if Cfg_ExtAcqAsLevel = 0. | Read/Write | 0 | 0
raP_Dvc_VlvMP | XCmd_Rel | Input | BOOL | CmdSrc.XCmd_Rel | 0 | Decimal | 0 | 0 | External command to release ownership if Cfg_ExtAcqAsLevel = 0 (External to Operator/Program/Override/Maintenance). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | XCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to clear shed latches and cleared alarms. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_VlvMP | XCmd_ResetAckAll | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to acknowledge and reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_LgxChangeDet | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Inp_Reset | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Reset detected changes and cleared latched alarms. | Read/Write | 0 | 0
raP_Dvc_LgxChangeDet | Inp_InitializeReq | Input | BOOL |  | 1 | Decimal | 0 | 0 | Use this request when reinitializing. | Read/Write | 0 | 0
raP_Dvc_LgxChangeDet | Inp_RdyReset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Related object, reset by this object, is ready to be reset. | Read/Write | 0 | 0
raP_Dvc_LgxChangeDet | Cfg_AllowDisable | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Maintenance to disable alarms. | Read/Write | 0 | 0
raP_Dvc_LgxChangeDet | Cfg_AllowShelve | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Operator to shelve alarms. | Read/Write | 0 | 0
raP_Dvc_LgxChangeDet | Cfg_HasMoreObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with more info is available. | Read/Write | 0 | 0
raP_Dvc_LgxChangeDet | Cfg_CnfrmReqd | Input | SINT |  | 0 | Decimal | 0 | 0 | Operator Command Confirmation Required. Represents the type of command confirmation required. 0 = None, 1 = Command confirmation required, 2 = Performer e-signature required, 3 = Performer and approver e-signature required. | Read/Write | 0 | 0
raP_Dvc_LgxChangeDet | Cfg_UpdateTime | Input | REAL |  | 5 | Float | 0 | 1 | Update (poll) time for change data, valid = 1.0 to 60.0 seconds. | Read/Write | 0 | 0
raP_Dvc_LgxCPU_5x80 | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Dvc_LgxCPU_5x80 | Inp_InitializeReq | Input | BOOL |  | 1 | Decimal | 0 | 0 | Use this request when reinitializing. | Read/Write | 0 | 0
raP_Dvc_LgxCPU_5x80 | Cfg_HasMoreObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with more info is available. | Read/Write | 0 | 0
raP_Dvc_LgxCPU_5x80 | Cfg_CtrlrSlotNumber | Input | INT |  | 0 | Decimal | 0 | 1 | Controller Slot Number in local chassis, valid 0 to chassis size. | Read/Write | 0 | 0
raP_Dvc_LgxCPU_5x80 | Cfg_UpdateTime | Input | REAL |  | 10 | Float | 0 | 1 | Update (poll) time for CPU data in seconds, valid 0.0 to 2147483.0. Values less than 2 seconds not recommended. | Read/Write | 0 | 0
raP_Dvc_LgxCPU_5x80 | PCmd_Enable | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to enable collection of data. | Read/Write | 0 | 0
raP_Dvc_LgxCPU_5x80 | PCmd_Disable | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to disable collection of data. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Inp_Reset | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Reset shed latches and cleared alarms. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | Inp_Parent_IO_OK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Parent (grandparent, etc.) module (adapter) I/O OK, 0 = Faulted. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | Inp_Parent_IO_AlmGate | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Parent: OK to alarm I/O Fault, 0 = parent is raising alarm, inhibit this object's I/O Fault alarm. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | Inp_AnyChanFault | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Any I/O channel on this module is faulted, 0 = All channels OK. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | Inp_AnyChanUncertain | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Any I/O channel on this module is uncertain, 0 = All channels OK. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | Inp_InitializeReq | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Request to initialize the instruction. The instruction is normally initialized in instruction first run. Use this request when reinitialization is needed. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | Inp_RdyReset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Related object, reset by this object, is ready to be reset. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | Cfg_AllowDisable | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Maintenance to disable alarms. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | Cfg_AllowShelve | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Operator to shelve alarms. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | Cfg_HasMoreObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with more information is available, enable navigation. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | Cfg_CnfrmReqd | Input | SINT |  | 0 | Decimal | 0 | 0 | Operator Command Confirmation Required. Represents the type of command confirmation required. 0 = None, 1 = Command confirmation required, 2 = Performer e-signature required, 3 = Performer and approver e-signature required. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | Cfg_ModuleFaultOnDly | Input | REAL |  | 1 | Float | 0 | 0 | On-Delay time for Module Fault alarm / status. Valid = 0.0 to 2147483.0 seconds. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | Set_VirtualConnectedSts | Input | BOOL |  | 0 | Decimal | 0 | 0 | Connection status used in Virtual (Sts_Virtual is 1). If the instruction is not in Virtual, 1 = connected, 0 = faulted. This setting tracks the physical connection status for bumpless transfer to Virtual. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | PCmd_Virtual | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to select Virtual (simulated) module connection status. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | PCmd_Physical | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to select Physical module connection status (not simulated). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | PCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to reset all alarms requiring reset. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | XCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to clear shed latches and cleared alarms. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | XCmd_ResetAckAll | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to acknowledge and reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Dvc_LgxRedun | Inp_InitializeReq | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Request to initialize the instruction. The instruction is normally initialized in instruction first run. Use this request when reinitialization is needed. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Inp_RdyReset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Related object, reset by this object, is ready to be reset. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Inp_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset cleared latched alarms. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_AllowDisable | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Maintenance to disable alarms. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_AllowShelve | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Operator to shelve alarms. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_AllowOCmdSync | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow OCmd_Sync to initiate sync of primary to secondary. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_AllowXCmdSync | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow XCmd_Sync to initiate sync of primary to secondary. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_AllowMCmdSwitchover | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Allow MCmd_Switchover to initiate switch to secondary. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_AllowXCmdSwitchover | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Allow XCmd_Switchover to initiate switch to secondary. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_Select_A_B | Input | BOOL |  | 0 | Decimal | 0 | 0 | Selects which chassis is A and which is B; if reversed on HMI, flip this bit. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_RackSize | Input | SINT |  | 7 | Decimal | 0 | 0 | Number of slots in redundant chassis, for example: 4, 7, 10, 13, or 17. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot00 | Input | SINT |  | 5 | Decimal | 0 | 0 | Type of Module in Slot 0: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot01 | Input | SINT |  | 1 | Decimal | 0 | 0 | Type of Module in Slot 1: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot02 | Input | SINT |  | 3 | Decimal | 0 | 0 | Type of Module in Slot 2: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot03 | Input | SINT |  | 4 | Decimal | 0 | 0 | Type of Module in Slot 3: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot04 | Input | SINT |  | 0 | Decimal | 0 | 0 | Type of Module in Slot 4: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot05 | Input | SINT |  | 0 | Decimal | 0 | 0 | Type of Module in Slot 5: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot06 | Input | SINT |  | 0 | Decimal | 0 | 0 | Type of Module in Slot 6: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot07 | Input | SINT |  | 0 | Decimal | 0 | 0 | Type of Module in Slot 7: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot08 | Input | SINT |  | 0 | Decimal | 0 | 0 | Type of Module in Slot 8: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot09 | Input | SINT |  | 0 | Decimal | 0 | 0 | Type of Module in Slot 9: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot10 | Input | SINT |  | 0 | Decimal | 0 | 0 | Type of Module in Slot 10: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot11 | Input | SINT |  | 0 | Decimal | 0 | 0 | Type of Module in Slot 11: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot12 | Input | SINT |  | 0 | Decimal | 0 | 0 | Type of Module in Slot 12: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot13 | Input | SINT |  | 0 | Decimal | 0 | 0 | Type of Module in Slot 13: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot14 | Input | SINT |  | 0 | Decimal | 0 | 0 | Type of Module in Slot 14: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot15 | Input | SINT |  | 0 | Decimal | 0 | 0 | Type of Module in Slot 15: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_eSlot16 | Input | SINT |  | 0 | Decimal | 0 | 0 | Type of Module in Slot 16: 0 = filler, 1 = CLx, 2 = SRM, 3 = RM, 4 = CNet, 5 = ENet. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_HasMoreObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with more information is available, enable navigation. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | Cfg_CnfrmReqd | Input | SINT |  | 0 | Decimal | 0 | 0 | Operator Command Confirmation Required. Represents the type of command confirmation required. 0 = None, 1 = Command confirmation required, 2 = Performer e-signature required, 3 = Performer and approver e-signature required. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | PCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to reset cleared latched Alarms. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | XCmd_Sync | Input | BOOL |  | 0 | Decimal | 0 | 0 | External Command to initiate synchronization of primary to secondary. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | XCmd_Switchover | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to initiate switchover to secondary controller. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | XCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to reset cleared latched alarms. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_LgxRedun | XCmd_ResetAckAll | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to acknowledge and reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_LgxTaskMon | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Inp_InitializeReq | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Request to initialize the instruction. The instruction is normally initialized in instruction first run. Use this request when reinitialization is needed. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_LgxTaskMon | Inp_RdyReset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Related object, reset by this object, is ready to be reset. | Read/Write | 0 | 0
raP_Dvc_LgxTaskMon | Inp_Reset | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Reset cleared latched alarms. | Read/Write | 0 | 0
raP_Dvc_LgxTaskMon | Cfg_AllowDisable | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Maintenance to disable alarms. | Read/Write | 0 | 0
raP_Dvc_LgxTaskMon | Cfg_AllowShelve | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Operator to shelve alarms. | Read/Write | 0 | 0
raP_Dvc_LgxTaskMon | Cfg_PlanExecTime | Input | REAL |  | 3000 | Float | 0 | 0 | Expected Execution Time of Task (including interrupts) (milliseconds). | Read/Write | 0 | 0
raP_Dvc_LgxTaskMon | Cfg_HasMoreObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with more information is available, enable navigation. | Read/Write | 0 | 0
raP_Dvc_LgxTaskMon | Cfg_CnfrmReqd | Input | SINT |  | 0 | Decimal | 0 | 0 | Operator Command Confirmation Required. Represents the type of command confirmation required. 0 = None, 1 = Command confirmation required, 2 = Performer e-signature required, 3 = Performer and approver e-signature required. | Read/Write | 0 | 0
raP_Dvc_LgxTaskMon | PCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to reset cleared latched Alarms. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_LgxTaskMon | XCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to reset cleared latched alarms. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Dvc_LgxTaskMon | XCmd_ResetAckAll | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to acknowledge and reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_ArbitrationQ | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Opr_ArbitrationQ | Inp_InitializeReq | Input | BOOL |  | 0 | Decimal | 0 | 0 | Request to Initialize. | None | 0 | 0
raP_Opr_Area | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Opr_Area | Inp_InitializeReq | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Request to initialize the instruction. The instruction is normally initialized in instruction first run. Use this request when reinitialization is needed. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Area | Inp_EStop | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Emergency stop input ok. | Read/Write | 0 | 0
raP_Opr_Area | Inp_SStop | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Software stop input ok. | Read/Write | 0 | 0
raP_Opr_Area | Inp_ExtddAlmsUsed | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Tells HMI object is connected to Inp_ExtddAlmsAlm input. | Read/Write | 0 | 0
raP_Opr_Area | Inp_ExtddAlmsAlm | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarms active. | Read/Write | 0 | 0
raP_Opr_Area | Inp_ExtddAlmsAcked | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended Alarm Acknowledge. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_Area | Inp_ExtddAlmsAlmInh | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm is shelved, disabled or suppressed. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_Area | Inp_ExtddAlmsDisabled | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended Alarm Disabled. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_Area | Inp_ExtddAlmsShelved | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm shelved. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_Area | Inp_ExtddAlmsSuppressed | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm suppressed. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_Area | Inp_ExtddAlmsAlarmFault | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm error. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_Area | Inp_ExtddAlmsRdyReset | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = A latched extended alarm is ready to be reset. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_Area | Inp_ExtddAlmseNotify | Input | SINT |  | 0 | Decimal | 0 | 0 | Extended alarms status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. Highest active extended alarm value. | Read/Write | 0 | 0
raP_Opr_Area | Inp_ExtddAlmsDsply | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm severity value is greatest of all extended alarms active. Each bit represents an individual alarm. (0 - 31). | Read/Write | 0 | 0
raP_Opr_Area | Inp_ExtInh | Input | BOOL | CmdSrc.Inp_ExtInh | 0 | Decimal | 0 | 0 | 1 = Inhibit External acquisition, 0 = Allow External acquisition. | Read/Write | 0 | 0
raP_Opr_Area | Inp_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset all fault conditions and latched alarms. | Read/Write | 0 | 0
raP_Opr_Area | Inp_RdyReset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Related object, reset by this object, is ready to be reset. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_AllowDisable | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Allow Operator alarm disable, 0 = Disallow Operator alarm disable. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_AllowShelve | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Allow Operator alarm shelve, 0 = Disallow Operator alarm shelve. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_HasExtddAlmObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1= Extended alarms object confirmed in system. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_HasMoreObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with more info is available. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_HasSStopInp | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Software stop input is available. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_HasSStopUnit | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Software stop propagation on the bus is available. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_ShedOnExtddAlms | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Alarm on extended alarm; 0 = Alarm only on extended Alarm. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_ShedOnChildNotUsable | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Shed on child cannot be owned or is in a state that makes it unusable for parent; 0 = Child cannot be owned or is in a state that makes it unusable for parent indication only. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_ShedOnChildAlarm | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Shed on child alarm or alarm UnAckd; 0 = Child alarm active or UnAckd indication only. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_Child2BGoodTmr | Input | DINT |  | 5 | Decimal | 0 | 0 | Time to delay Child Acquisition check status (Seconds) | Read/Write | 0 | 0
raP_Opr_Area | Cfg_OwnerCmdSrc | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Command source follows owner. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_CascadeOwn | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Children will be owned when this object is owned. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_eKeepOwnerCmds | Input | SINT |  | 2 | Decimal | 0 | 0 | Ownership of module Ownership commands (enumeration): 0 = follows CmdSrc, 1 = Operator, 2 = Program, 3 = External. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_CnfrmReqd | Input | SINT |  | 0 | Decimal | 0 | 0 | Operator Command Confirmation Required. Represents the type of command confirmation required. 0 = None, 1 = Command confirmation required, 2 = Performer e-signature required, 3 = Performer and approver e-signature required. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_HasOper | Input | BOOL | CmdSrc.Cfg_HasOper | 1 | Decimal | 0 | 0 | 1 = Operator (unlocked) exists, can be selected. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_HasOperLocked | Input | BOOL | CmdSrc.Cfg_HasOperLocked | 1 | Decimal | 0 | 0 | 1 = Operator locked exists, can be selected. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_HasProg | Input | BOOL | CmdSrc.Cfg_HasProg | 1 | Decimal | 0 | 0 | 1 = Program (unlocked) exists, can be selected. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_HasProgLocked | Input | BOOL | CmdSrc.Cfg_HasProgLocked | 1 | Decimal | 0 | 0 | 1 = Program locked exists, can be selected. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_HasExt | Input | BOOL | CmdSrc.Cfg_HasExt | 0 | Decimal | 0 | 0 | 1 = External exists, can be selected. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_HasMaint | Input | BOOL | CmdSrc.Cfg_HasMaint | 1 | Decimal | 0 | 0 | 1 = Maintenance exists, can be selected. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_HasMaintOoS | Input | BOOL | CmdSrc.Cfg_HasMaintOoS | 1 | Decimal | 0 | 0 | 1 = Maintenance Out of Service exists, can be selected. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_OvrdOverLock | Input | BOOL | CmdSrc.Cfg_OvrdOverLock | 1 | Decimal | 0 | 0 | 1 = Override supersedes Program/Operator lock, 0 = Don't Override lock. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_ExtOverLock | Input | BOOL | CmdSrc.Cfg_ExtOverLock | 0 | Decimal | 0 | 0 | 1 = External supersedes Program/Operator lock, 0 = Don't Override lock. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_ProgPwrUp | Input | BOOL | CmdSrc.Cfg_ProgPwrUp | 0 | Decimal | 0 | 0 | 1 = Power up to Program, 0 = Power up to Operator. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_ProgNormal | Input | BOOL | CmdSrc.Cfg_ProgNormal | 0 | Decimal | 0 | 0 | Normal source: 1 = Program if no requests; 0 = Operator if no requests. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_PCmdPriority | Input | BOOL | CmdSrc.Cfg_PCmdPriority | 0 | Decimal | 0 | 0 | Command priority. 1 = Program commands win, 0 = Operator commands win. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_PCmdProgAsLevel | Input | BOOL | CmdSrc.Cfg_PCmdProgAsLevel | 0 | Decimal | 0 | 0 | 1 = PCmd_Prog used as a level. | Read/Write | 0 | 0
raP_Opr_Area | Cfg_PCmdLockAsLevel | Input | BOOL | CmdSrc.Cfg_PCmdLockAsLevel | 0 | Decimal | 0 | 0 | 1 = PCmd_Lock used as a level (1 = Lock, 0 = Unlock). | Read/Write | 0 | 0
raP_Opr_Area | Cfg_ExtAcqAsLevel | Input | BOOL | CmdSrc.Cfg_ExtAcqAsLevel | 0 | Decimal | 0 | 0 | 1 = XCmd_Acq used as level (1 = Acquire, 0 = Release). | Read/Write | 0 | 0
raP_Opr_Area | PCmd_Oper | Input | BOOL | CmdSrc.PCmd_Oper | 0 | Decimal | 0 | 0 | Program command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Area | PCmd_Prog | Input | BOOL | CmdSrc.PCmd_Prog | 0 | Decimal | 0 | 0 | Program command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Area | PCmd_Lock | Input | BOOL | CmdSrc.PCmd_Lock | 0 | Decimal | 0 | 0 | Program command to lock Program (disallow Operator). The instruction clears this operand automatically if Cfg_PCmdLockAsLevel = 0. | Read/Write | 0 | 0
raP_Opr_Area | PCmd_Unlock | Input | BOOL | CmdSrc.PCmd_Unlock | 0 | Decimal | 0 | 0 | Program command to unlock Program (allow Operator to acquire). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Area | PCmd_Normal | Input | BOOL | CmdSrc.PCmd_Normal | 0 | Decimal | 0 | 0 | Program command to select normal command source (Operator or Program). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Area | PCmd_OwnerAcq | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to acquire child command source. | Read/Write | 0 | 0
raP_Opr_Area | PCmd_OwnerRel | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to release child command source. | Read/Write | 0 | 0
raP_Opr_Area | PCmd_UnbindChildren | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to unbind children command source. | Read/Write | 0 | 0
raP_Opr_Area | PCmd_Physical | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to select Physical device operation. (not simulated). | Read/Write | 0 | 0
raP_Opr_Area | PCmd_Virtual | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to select Virtual (simulated) device operation. | Read/Write | 0 | 0
raP_Opr_Area | PCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to reset all alarms request. | Read/Write | 0 | 0
raP_Opr_Area | PCmd_SuppressAllAlms | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to suppress all parent and child alarms if applicable. (Bus Mask set) | Read/Write | 0 | 0
raP_Opr_Area | PCmd_UnSuppressAllAlms | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to unsuppress all parent and child alarms if applicable. (Bus Mask set) | Read/Write | 0 | 0
raP_Opr_Area | XCmd_Acq | Input | BOOL | CmdSrc.XCmd_Acq | 0 | Decimal | 0 | 0 | External command to acquire ownership (Operator/Program/Override/Maintenance to External). The instruction clears this operand automatically if Cfg_ExtAcqAsLevel = 0. | Read/Write | 0 | 0
raP_Opr_Area | XCmd_Rel | Input | BOOL | CmdSrc.XCmd_Rel | 0 | Decimal | 0 | 0 | External command to release ownership if Cfg_ExtAcqAsLevel = 0 (External to Operator/Program/Override/Maintenance). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Area | XCmd_OwnerAcq | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to acquire child command source. | Read/Write | 0 | 0
raP_Opr_Area | XCmd_OwnerRel | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to release child command source. | Read/Write | 0 | 0
raP_Opr_Area | XCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | External Command to reset shed latches and cleared alarms. | Read/Write | 0 | 0
raP_Opr_Area | XCmd_ResetAckAll | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to acknowledge and reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EMGen | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Opr_EMGen | Inp_InitializeReq | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Request to initialize the instruction. The instruction is normally initialized in instruction first run. Use this request when reinitialization is needed. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_St | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | Reference process state (bitwise). | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_StepHold | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Hold step from advancing to next requested step. | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_RdyOk | Input | DINT |  | 2#1111_1111_1111_1111_1111_1111_1111_1111 | Binary | 0 | 0 | 1 = Input condition ready. Mapped to relative Rdy bit: Inp_RdyOk.(x) = Rdy.(x). | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_RdyOkProg | Input | DINT |  | 2#1111_1111_1111_1111_1111_1111_1111_1111 | Binary | 0 | 0 | 1 = Input condition ready. Mapped to relative Rdy Prog bit: Inp_RdyOkProg.(x) = Rdy_Prog.(x). | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_PermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Permissive bypassable input ok. | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_NBPermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Permissive non-bypassable input ok. | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_IntlkOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = By-passable interlock ok. Used to input all by-passable interlock conditions for a particular instance. This Input can be connected to an external multiplexer block (Cfg_HasIntlkObj). This input will be ignored when bypass interlocks and permissives mode is active. | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_NBIntlkOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Non by-passable interlock ok. Used to input all non by-passable interlock conditions for a particular instance. This Input can be connected to an external multiplexer block (Cfg_HasIntlkObj). | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_IntlkAvailable | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Interlock availability ok. | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_IntlkTripInh | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Inhibit interlock trip status. | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_RdyReset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Related object, reset by this object, is ready to be reset. | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_DvcAlms | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Bypassable device alarm active. | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_NBDvcAlms | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Non-bypassable device alarm active. | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_ExtddAlmsUsed | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Tells HMI object is connected to Inp_ExtddAlmsAlm input. | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_ExtddAlmsAlm | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarms active. | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_ExtddAlmsAcked | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended Alarm Acknowledge. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_ExtddAlmsAlmInh | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm is shelved, disabled or suppressed. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_ExtddAlmsDisabled | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended Alarm Disabled. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_ExtddAlmsShelved | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm shelved. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_ExtddAlmsSuppressed | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm suppressed. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_ExtddAlmsAlarmFault | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm error. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_ExtddAlmsRdyReset | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = A latched extended alarm is ready to be reset. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_ExtddAlmseNotify | Input | SINT |  | 0 | Decimal | 0 | 0 | Extended alarms status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. Highest active extended alarm value. | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_ExtddAlmsDsply | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm severity value is greatest of all extended alarms active. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_ExtInh | Input | BOOL | CmdSrc.Inp_ExtInh | 0 | Decimal | 0 | 0 | 1 = Inhibit External acquisition, 0 = Allow External acquisition. | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset all fault conditions and latched alarms. | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_EnableNavTrans | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Enable navigation to transition diagnostic object. | Read/Write | 0 | 0
raP_Opr_EMGen | Inp_PromptRdy | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 - Associated raP_Opr_Prompt is ready | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_AlmAllowCmd | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Allows operator command execution with active alarm condition. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_PermAllowCmd | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Allows operator command (x) execution with loss of permissive (x). | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_HasExtddAlmObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1= Extended alarms object confirmed in system. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_ShedOnExtddAlms | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Alarm on extended alarm; 0 = Alarm only on extended Alarm. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_ShedOnChildAlarm | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Shed on child alarm or alarm UnAckd; 0 = Child alarm active or UnAckd indication only. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_ShedOnChildNotUsable | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Shed on child cannot be owned or is in a state that makes it unusable for parent; 0 = Child cannot be owned or is in a state that makes it unusable for parent indication only. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_UseLegacyOwnership | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Use legacy ownership (PSetOwner) over the Bus. 0 = Use bBus ownership. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_Child2BGoodTmr | Input | DINT |  | 5 | Decimal | 0 | 0 | Time to delay Child Acquisition check status (Seconds) | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_NumPars | Input | SINT |  | 0 | Decimal | 0 | 0 | The equipment module may be configured to use external parameter objects. This value defines the number of parameters objects defined for use. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_NumRpts | Input | SINT |  | 0 | Decimal | 0 | 0 | The equipment module may be configured to use external report objects. This value defines the number of report objects defined for use. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_UserDINT1 | Input | DINT |  | 0 | Decimal | 0 | 0 | User definable DINT Input 1. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_UserDINT2 | Input | DINT |  | 0 | Decimal | 0 | 0 | User definable DINT Input 2. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_UserReal1 | Input | REAL |  | 0 | Float | 0 | 0 | User definable REAL Input 1. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_UserReal2 | Input | REAL |  | 0 | Float | 0 | 0 | User definable REAL Input 2. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_HasParCmds | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = This equipment module has the parameter operator commands. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_HasRptCmds | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = This equipment module has the report operator commands. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_HasPrompt | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Has associated raP_Opr_Prompt. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_HasDetailDisplay | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Associated detail display for Instance. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_HasIntlkObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI equipment module is connected to Inp_Intlk inputs. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_HasPermObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI equipment module is connected to Inp_Perm inputs. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_OwnerCmdSrc | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Command source follows owner. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_CascadeOwn | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Children will be owned when this object is owned. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_ExtAcqAsLevel | Input | BOOL | CmdSrc.Cfg_ExtAcqAsLevel | 0 | Decimal | 0 | 0 | 1 = XCmd_Acq used as level (1 = Acquire, 0 = Release). | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_ExtOverLock | Input | BOOL | CmdSrc.Cfg_ExtOverLock | 0 | Decimal | 0 | 0 | 1 = External supersedes Program/Operator lock, 0 = Don't Override lock. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_HasExt | Input | BOOL | CmdSrc.Cfg_HasExt | 0 | Decimal | 0 | 0 | 1 = External exists, can be selected. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_HasMaint | Input | BOOL | CmdSrc.Cfg_HasMaint | 1 | Decimal | 0 | 0 | 1 = Maintenance exists, can be selected. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_HasMaintOoS | Input | BOOL | CmdSrc.Cfg_HasMaintOoS | 1 | Decimal | 0 | 0 | 1 = Maintenance Out of Service exists, can be selected. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_HasOper | Input | BOOL | CmdSrc.Cfg_HasOper | 1 | Decimal | 0 | 0 | 1 = Operator (unlocked) exists, can be selected. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_HasOperLocked | Input | BOOL | CmdSrc.Cfg_HasOperLocked | 1 | Decimal | 0 | 0 | 1 = Operator locked exists, can be selected. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_HasProg | Input | BOOL | CmdSrc.Cfg_HasProg | 1 | Decimal | 0 | 0 | 1 = Program (unlocked) exists, can be selected. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_HasProgLocked | Input | BOOL | CmdSrc.Cfg_HasProgLocked | 1 | Decimal | 0 | 0 | 1 = Program locked exists, can be selected. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_OvrdOverLock | Input | BOOL | CmdSrc.Cfg_OvrdOverLock | 1 | Decimal | 0 | 0 | 1 = Override supersedes Program/Operator lock, 0 = Don't Override lock. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_PCmdLockAsLevel | Input | BOOL | CmdSrc.Cfg_PCmdLockAsLevel | 0 | Decimal | 0 | 0 | 1 = PCmd_Lock used as a level (1 = Lock, 0 = Unlock). | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_PCmdPriority | Input | BOOL | CmdSrc.Cfg_PCmdPriority | 0 | Decimal | 0 | 0 | Command priority. 1 = Program commands win, 0 = Operator commands win. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_PCmdProgAsLevel | Input | BOOL | CmdSrc.Cfg_PCmdProgAsLevel | 0 | Decimal | 0 | 0 | 1 = PCmd_Prog used as a level. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_ProgNormal | Input | BOOL | CmdSrc.Cfg_ProgNormal | 0 | Decimal | 0 | 0 | Normal source: 1 = Program if no requests; 0 = Operator if no requests. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_ProgPwrUp | Input | BOOL | CmdSrc.Cfg_ProgPwrUp | 0 | Decimal | 0 | 0 | 1 = Power up to Program, 0 = Power up to Operator. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_AllowDisable | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Allow Operator alarm disable, 0 = Disallow Operator alarm disable. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_AllowShelve | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Allow Operator alarm shelve, 0 = Disallow Operator alarm shelve. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_Class | Input | BOOL |  | 0 | Decimal | 0 | 0 | Extended Property of this parameter is used to define a Class of an EM. | Read Only | 0 | 0
raP_Opr_EMGen | Cfg_HasMoreObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with more info is available. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_HasDvcAlmsObjNav | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with device alarm info is available. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_ShedOnDvcAlms | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Stop equipment module and alarm on device alarm; 0 = Alarm only on device alarm. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_ShedOnRptData | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Stop equipment module and alarm on report data; 0 = Alarm only on report data. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_WaitRptData | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Wait for report data to be collected. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_CnfrmReqd | Input | SINT |  | 0 | Decimal | 0 | 0 | Operator Command Confirmation Required. Represents the type of command confirmation required. 0 = None, 1 = Command confirmation required, 2 = Performer e-signature required, 3 = Performer and approver e-signature required. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_IdleState | Input | SINT |  | 0 | Decimal | 0 | 0 | Configured Idle State (bitwise). | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_RunState | Input | SINT |  | 1 | Decimal | 0 | 0 | Configured Run State (bitwise). | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_CompleteState | Input | SINT |  | 2 | Decimal | 0 | 0 | Configured Complete State (bitwise). | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_eKeepCmds | Input | SINT |  | 0 | Decimal | 0 | 0 | Ownership of module commands (enumeration): 0 = follows CmdSrc, 1 = Operator, 2 = Program, 3 = External. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_eKeepOwnerCmds | Input | SINT |  | 2 | Decimal | 0 | 0 | Ownership of module Ownership commands (enumeration): 0 = follows CmdSrc, 1 = Operator, 2 = Program, 3 = External. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_eKeepStep | Input | SINT |  | 0 | Decimal | 0 | 0 | Ownership of Setpoint (enumeration): 0 = follows CmdSrc, 1 = Operator, 2 = Program, 3 = External. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_eKeepVSM | Input | SINT |  | 2 | Decimal | 0 | 0 | Ownership of VSM (enumeration): 0 = follows CmdSrc, 1 = Operator, 2 = Program, 3 = External. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_eKeepPar | Input | SINT |  | 2 | Decimal | 0 | 0 | Ownership of parameters (enumeration): 0 = follows CmdSrc, 1 = Operator, 2 = Program, 3 = External. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_eKeepRpt | Input | SINT |  | 2 | Decimal | 0 | 0 | Ownership of reports (enumeration): 0 = follows CmdSrc, 1 = Operator, 2 = Program, 3 = External. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_NRdyState | Input | SINT |  | -1 | Decimal | 0 | 0 | Configured State to transition to on Not Ready condition (bitwise). The value will set the associated bit within the Command word. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_IntlkTripState | Input | SINT |  | -1 | Decimal | 0 | 0 | Configured State to transition to on Interlock trip condition (bitwise). The value will set the associated bit within the Command word. | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_ShedOnIntlk | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Stop equipment module and alarm on interlock trip; 0 = Stop equipment module state (bitwise). | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_RestartState | Input | DINT |  | 0 | Decimal | 0 | 0 | Configured Restart State (bitwise). | Read/Write | 0 | 0
raP_Opr_EMGen | Cfg_UnqID | Input | DINT |  | 0 | Decimal | 0 | 0 | HMI none bus object index. | Read Only | 0 | 0
raP_Opr_EMGen | PSet_HoldIndx | Input | INT |  | 0 | Decimal | 0 | 0 | Program setting of process step number hold index to return at re-start. | Read/Write | 0 | 0
raP_Opr_EMGen | PSet_Step | Input | INT |  | 0 | Decimal | 0 | 0 | Program setting of process step number. | Read/Write | 0 | 0
raP_Opr_EMGen | PSet_StepDesc | Input | INT |  | 0 | Decimal | 0 | 0 | Program setting of process step number description for display. | Read/Write | 0 | 0
raP_Opr_EMGen | PSet_Summary | Input | INT |  | 0 | Decimal | 0 | 0 | Program setting of process summary. | Read/Write | 0 | 0
raP_Opr_EMGen | PSet_OrganizedStep | Input | INT |  | 0 | Decimal | 0 | 0 | Program setting of process step number. | Read/Write | 0 | 0
raP_Opr_EMGen | PSet_Owner | Input | DINT |  | 0 | Decimal | 0 | 0 | Program owner request ID (non-zero) or release (zero). | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | Program command to State (bitwise). | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_StateForce | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to complete state request. | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_Lock | Input | BOOL | CmdSrc.PCmd_Lock | 0 | Decimal | 0 | 0 | Program command to lock Program (disallow Operator). The instruction clears this operand automatically if Cfg_PCmdLockAsLevel = 0. | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_Normal | Input | BOOL | CmdSrc.PCmd_Normal | 0 | Decimal | 0 | 0 | Program command to select normal command source (Operator or Program). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_Oper | Input | BOOL | CmdSrc.PCmd_Oper | 0 | Decimal | 0 | 0 | Program command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_Prog | Input | BOOL | CmdSrc.PCmd_Prog | 0 | Decimal | 0 | 0 | Program command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_Unlock | Input | BOOL | CmdSrc.PCmd_Unlock | 0 | Decimal | 0 | 0 | Program command to unlock Program (allow Operator to acquire). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_ParCapture | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to capture initial parameter. | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_ParClear | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to clear parameter. | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_ParRestore | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to restore initial parameter. | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_RptCapture | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to capture initial report. | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_RptClear | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to clear report. | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_RptRestore | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to restore initial report. | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_OwnerAcq | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to acquire child command source. | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_OwnerRel | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to release child command source. | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_UnbindChildren | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to unbind children command source. | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to reset all alarms request. | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_SuppressAllAlms | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to suppress all parent and child alarms if applicable. (Bus Mask set) | Read/Write | 0 | 0
raP_Opr_EMGen | PCmd_UnSuppressAllAlms | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to unsuppress all parent and child alarms if applicable. (Bus Mask set) | Read/Write | 0 | 0
raP_Opr_EMGen | XCmd | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | External command to State (bitwise). | Read/Write | 0 | 0
raP_Opr_EMGen | XCmd_StateForce | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to force state. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EMGen | XCmd_Acq | Input | BOOL | CmdSrc.XCmd_Acq | 0 | Decimal | 0 | 0 | External command to acquire ownership (Operator/Program/Override/Maintenance to External). The instruction clears this operand automatically if Cfg_ExtAcqAsLevel = 0. | Read/Write | 0 | 0
raP_Opr_EMGen | XCmd_Rel | Input | BOOL | CmdSrc.XCmd_Rel | 0 | Decimal | 0 | 0 | External command to release ownership if Cfg_ExtAcqAsLevel = 0 (External to Operator/Program/Override/Maintenance). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EMGen | XCmd_OwnerAcq | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to acquire child command source. | Read/Write | 0 | 0
raP_Opr_EMGen | XCmd_OwnerRel | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to release child command source. | Read/Write | 0 | 0
raP_Opr_EMGen | XCmd_ParCapture | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to capture initial parameter. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EMGen | XCmd_ParClear | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to clear parameter. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EMGen | XCmd_ParRestore | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to restore initial parameter. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EMGen | XCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to reset shed latches and cleared alarms. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EMGen | XCmd_ResetAckAll | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to acknowledge and reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EMGen | XCmd_RptCapture | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to capture initial report. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EMGen | XCmd_RptClear | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to clear report. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EMGen | XCmd_RptRestore | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to restore initial report. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Opr_EPGen | Inp_InitializeReq | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Request to initialize the instruction. The instruction is normally initialized in instruction first run. Use this request when reinitialization is needed. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_StepHold | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Hold step from advancing to next requested step. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_PermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Permissive bypassable input ok. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_NBPermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Permissive non-bypassable input ok. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_IntlkOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = By-passable interlock ok. Used to input all by-passable interlock conditions for a particular instance. This Input can be connected to an external multiplexer block (Cfg_HasIntlkObj). This input will be ignored when bypass interlocks and permissives mode is active. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_NBIntlkOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Non by-passable interlock ok. Used to input all non by-passable interlock conditions for a particular instance. This Input can be connected to an external multiplexer block (Cfg_HasIntlkObj). | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_IntlkAvailable | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Interlock availability ok. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_IntlkTripInh | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Inhibit interlock trip status. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_RdyReset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Related object, reset by this object, is ready to be reset. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_DvcAlms | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Bypassable device alarm active. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_NBDvcAlms | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Non-bypassable device alarm active. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_Active | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Phase synchronization active. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_Done | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Phase synchronization done. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_Waiting | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Phase synchronization waiting. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_ExtddAlmsUsed | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Tells HMI object is connected to Inp_ExtddAlmsAlm input. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_ExtddAlmsAlm | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarms active. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_ExtddAlmsAcked | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended Alarm Acknowledge. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_ExtddAlmsAlmInh | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm is shelved, disabled or suppressed. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_ExtddAlmsDisabled | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended Alarm Disabled. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_ExtddAlmsShelved | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm shelved. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_ExtddAlmsSuppressed | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm suppressed. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_ExtddAlmsAlarmFault | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm error. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_ExtddAlmsRdyReset | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = A latched extended alarm is ready to be reset. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_ExtddAlmseNotify | Input | SINT |  | 0 | Decimal | 0 | 0 | Extended alarms status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. Highest active extended alarm value. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_ExtddAlmsDsply | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm severity value is greatest of all extended alarms active. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_ExtInh | Input | BOOL | CmdSrc.Inp_ExtInh | 0 | Decimal | 0 | 0 | 1 = Inhibit External acquisition, 0 = Allow External acquisition. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset all fault conditions and latched alarms. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_EnableNavTrans | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Enable navigation to transition diagnostic object. | Read/Write | 0 | 0
raP_Opr_EPGen | Inp_PromptRdy | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 - Associated raP_Opr_Prompt is ready | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasExtddAlmObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1= Extended alarms object confirmed in system. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_ShedOnExtddAlms | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Alarm on extended alarm, Activate Stop Phase; 0 = Alarm only on extended Alarm. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_ShedOnChildAlarm | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Shed on child alarm or alarm UnAckd, Activate Stop Phase; 0 = Child alarm active or UnAckd indication only. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_ShedOnChildNotUsable | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Shed on child cannot be owned or is in a state that makes it unusable for parent, Activate Stop Phase; 0 = Child cannot be owned or is in a state that makes it unusable for parent indication only. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_ShedOnAlm | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Allows operator command execution with active alarm condition. Active Stop Phase. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_ShedOnSStop | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Shed equipment phase and alarm on SStop; 0 = Alarm only on report data. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_RptDataHold | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Hold equipment phase and alarm on report data alarm, Activate Hold Phase; 0 = Alarm only on report data alarm. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_UseLegacyOwnership | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Use legacy ownership (PSetOwner) over the Bus. 0 = Use bBus ownership. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasParCmds | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = This equipment phase has the parameter operator commands. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasRptCmds | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = This equipment phase has the report operator commands. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasDetailDisplay | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Associated detail display for Instance. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_NumPars | Input | INT |  | 0 | Decimal | 0 | 0 | The equipment phase may be configured to use external parameter objects. This value defines the number of parameters objects defined for use. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_NumRpts | Input | INT |  | 0 | Decimal | 0 | 0 | The equipment phase may be configured to use external report objects. This value defines the number of report objects defined for use. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_AlmIssuesHold | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Allows operator command execution with active alarm condition. Activate Hold Phase. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_ChildAlarmIssuesHold | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Hold on child alarm or alarm UnAckd, Activate Hold Phase; 0 = Child alarm active or UnAckd indication only. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_ChildNotUsableIssuesHold | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Hold on child cannot be owned or is in a state that makes it unusable for parent, Activate Hold Phase; 0 = Child cannot be owned or is in a state that makes it unusable for parent indication only. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_DvcAlmsIssuesHold | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Hold equipment phase and alarm on device alarm, Activate Hold Phase; 0 = Alarm only on device alarm. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_ExtddAlmsIssuesHold | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Alarm on extended alarm, Activate Hold Phase,; 0 = Alarm only on extended Alarm. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_IntlkIssuesHold | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Hold on Interlock trip, Activate Hold Phase.; 0 = Interlock tip active or UnAckd indication only. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_ExtSeq | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = This Phase has an External Sequencer Associated to it (FTBatch). | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasIntlkObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI equipment phase is connected to Inp_Intlk inputs. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasPause | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = This equipment phase has the pause option. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasPermObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI equipment phase is connected to Inp_Perm inputs. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_LoadDfltSteps | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Load default step numbers when the phase state initially changes. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_MapAlmToPhs | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Map alarm codes from equipment phase to the phase PFL codes. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_MskStFrmPhs | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Mask hold state from phase. Available with external sequencer only. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_AllowDisable | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Allow Operator alarm disable, 0 = Disallow Operator alarm disable. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_AllowShelve | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Allow Operator alarm shelve, 0 = Disallow Operator alarm shelve. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_Class | Input | BOOL |  | 0 | Decimal | 0 | 0 | Parameter will be used to define a Class of an EP. | Read Only | 0 | 0
raP_Opr_EPGen | Cfg_SStopIssuesHold | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Stop equipment phase and alarm on report data; 0 = Alarm only on report data. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_OwnerCmdSrc | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Command source follows owner. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_CascadeOwn | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Children will be owned when this object is owned. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasMaintOoS | Input | BOOL | CmdSrc.Cfg_HasMaintOoS | 1 | Decimal | 0 | 0 | 1 = Maintenance Out of Service exists, can be selected. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_ExtAcqAsLevel | Input | BOOL | CmdSrc.Cfg_ExtAcqAsLevel | 0 | Decimal | 0 | 0 | 1 = XCmd_Acq used as level (1 = Acquire, 0 = Release). | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_ExtOverLock | Input | BOOL | CmdSrc.Cfg_ExtOverLock | 0 | Decimal | 0 | 0 | 1 = External supersedes Program/Operator lock, 0 = Don't Override lock. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasExt | Input | BOOL | CmdSrc.Cfg_HasExt | 0 | Decimal | 0 | 0 | 1 = External exists, can be selected. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasMaint | Input | BOOL | CmdSrc.Cfg_HasMaint | 1 | Decimal | 0 | 0 | 1 = Maintenance exists, can be selected. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasOper | Input | BOOL | CmdSrc.Cfg_HasOper | 1 | Decimal | 0 | 0 | 1 = Operator (unlocked) exists, can be selected. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasOperLocked | Input | BOOL | CmdSrc.Cfg_HasOperLocked | 1 | Decimal | 0 | 0 | 1 = Operator locked exists, can be selected. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasProg | Input | BOOL | CmdSrc.Cfg_HasProg | 1 | Decimal | 0 | 0 | 1 = Program (unlocked) exists, can be selected. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasProgLocked | Input | BOOL | CmdSrc.Cfg_HasProgLocked | 1 | Decimal | 0 | 0 | 1 = Program locked exists, can be selected. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_OvrdOverLock | Input | BOOL | CmdSrc.Cfg_OvrdOverLock | 1 | Decimal | 0 | 0 | 1 = Override supersedes Program/Operator lock, 0 = Don't Override lock. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_PCmdLockAsLevel | Input | BOOL | CmdSrc.Cfg_PCmdLockAsLevel | 0 | Decimal | 0 | 0 | 1 = PCmd_Lock used as a level (1 = Lock, 0 = Unlock). | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_PCmdPriority | Input | BOOL | CmdSrc.Cfg_PCmdPriority | 0 | Decimal | 0 | 0 | Command priority. 1 = Program commands win, 0 = Operator commands win. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_PCmdProgAsLevel | Input | BOOL | CmdSrc.Cfg_PCmdProgAsLevel | 0 | Decimal | 0 | 0 | 1 = PCmd_Prog used as a level. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_ProgNormal | Input | BOOL | CmdSrc.Cfg_ProgNormal | 0 | Decimal | 0 | 0 | Normal source: 1 = Program if no requests; 0 = Operator if no requests. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_ProgPwrUp | Input | BOOL | CmdSrc.Cfg_ProgPwrUp | 0 | Decimal | 0 | 0 | 1 = Power up to Program, 0 = Power up to Operator. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasPrompt | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Has associated raP_Opr_Prompt. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasMoreObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with more info is available. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_ShedOnDvcAlms | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Stop equipment phase and alarm on device alarm; 0 = Alarm only on device alarm. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_ShedOnIntlk | Input | BOOL |  | 2#1 | Binary | 0 | 0 | 1 = Shed on Interlock trip, Activate Hold Phase.; 0 = Interlock trip active or UnAckd indication only. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_HasDvcAlmsObjNav | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with device alarm info is available. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_ShedOnRptData | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Stop equipment phase and alarm on report data alarm; 0 = Alarm only on report data alarm. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_WaitRptData | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1=Wait for report data to be collected. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_Child2BGoodTmr | Input | DINT |  | 5 | Decimal | 0 | 0 | Time to delay Child Acquisition check status (Seconds) | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_CnfrmReqd | Input | SINT |  | 0 | Decimal | 0 | 0 | Operator Command Confirmation Required. Represents the type of command confirmation required. 0 = None, 1 = Command confirmation required, 2 = Performer e-signature required, 3 = Performer and approver e-signature required. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_eKeepCmds | Input | SINT |  | 0 | Decimal | 0 | 0 | Ownership of module commands (enumeration): 0 = follows CmdSrc, 1 = Operator, 2 = Program, 3 = External. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_eKeepOwnerCmds | Input | SINT |  | 2 | Decimal | 0 | 0 | Ownership of module Ownership commands (enumeration): 0 = follows CmdSrc, 1 = Operator, 2 = Program, 3 = External. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_eKeepStep | Input | SINT |  | 0 | Decimal | 0 | 0 | Ownership of Setpoint (enumeration): 0 = follows CmdSrc, 1 = Operator, 2 = Program, 3 = External. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_eKeepPar | Input | SINT |  | 2 | Decimal | 0 | 0 | Ownership of parameters (enumeration): 0 = follows CmdSrc, 1 = Operator, 2 = Program, 3 = External. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_eKeepRpt | Input | SINT |  | 2 | Decimal | 0 | 0 | Ownership of reports (enumeration): 0 = follows CmdSrc, 1 = Operator, 2 = Program, 3 = External. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_UserDINT1 | Input | DINT |  | 0 | Decimal | 0 | 0 | User definable DINT Input 1. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_UserDINT2 | Input | DINT |  | 0 | Decimal | 0 | 0 | User definable DINT Input 2. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_UserReal1 | Input | REAL |  | 0 | Float | 0 | 0 | User definable REAL Input 1. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_UserReal2 | Input | REAL |  | 0 | Float | 0 | 0 | User definable REAL Input 2. | Read/Write | 0 | 0
raP_Opr_EPGen | Cfg_UnqID | Input | DINT |  | 0 | Decimal | 0 | 0 | HMI none bus object index. | Read Only | 0 | 0
raP_Opr_EPGen | PSet_Step | Input | INT |  | 0 | Decimal | 0 | 0 | Program setting of process step number. | Read/Write | 0 | 0
raP_Opr_EPGen | PSet_StepDesc | Input | INT |  | 0 | Decimal | 0 | 0 | Program setting of process step number description for display. | Read/Write | 0 | 0
raP_Opr_EPGen | PSet_Summary | Input | INT |  | 0 | Decimal | 0 | 0 | Program setting of process summary. | Read/Write | 0 | 0
raP_Opr_EPGen | PSet_HoldIndx | Input | INT |  | 0 | Decimal | 0 | 0 | Program setting of process step number hold index to return at re-start. | Read/Write | 0 | 0
raP_Opr_EPGen | PSet_AttchRslts | Input | DINT |  | 0 | Decimal | 0 | 0 | Program setting of phase attach (Ownership) results. | Read/Write | 0 | 0
raP_Opr_EPGen | PSet_CmmndRslts | Input | DINT |  | 0 | Decimal | 0 | 0 | Program setting of phase command results. | Read/Write | 0 | 0
raP_Opr_EPGen | PSet_OrganizedStep | Input | INT |  | 0 | Decimal | 0 | 0 | Program setting of process step number. | Read/Write | 0 | 0
raP_Opr_EPGen | PSet_Owner | Input | DINT |  | 0 | Decimal | 0 | 0 | Program owner request ID (non-zero) or release (zero). | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_Start | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to start request. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_Stop | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to stop request. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_Abort | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to abort request. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_Hold | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to hold request. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_Restart | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to Restart request. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_Pause | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to pause request. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_AutoPause | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to auto pause request. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_Resume | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to resume from paused request. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_StateForce | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to complete state request. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_ResetPhs | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to reset phase request. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_ParCapture | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to capture initial parameter. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_ParClear | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to clear parameter. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_ParRestore | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to restore initial parameter. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_RptCapture | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to capture initial report. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_RptClear | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to clear report. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_RptRestore | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to restore initial report. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_OwnerAcq | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to acquire child command source. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_OwnerRel | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to release child command source. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_UnbindChildren | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to unbind children command source. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to reset all alarms request. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_SuppressAllAlms | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to suppress all parent and child alarms if applicable. (Bus Mask set) | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_UnSuppressAllAlms | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to unsuppress all parent and child alarms if applicable. (Bus Mask set) | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_Lock | Input | BOOL | CmdSrc.PCmd_Lock | 0 | Decimal | 0 | 0 | Program command to lock Program (disallow Operator). The instruction clears this operand automatically if Cfg_PCmdLockAsLevel = 0. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_Normal | Input | BOOL | CmdSrc.PCmd_Normal | 0 | Decimal | 0 | 0 | Program command to select normal command source (Operator or Program). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_Oper | Input | BOOL | CmdSrc.PCmd_Oper | 0 | Decimal | 0 | 0 | Program command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_Prog | Input | BOOL | CmdSrc.PCmd_Prog | 0 | Decimal | 0 | 0 | Program command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | PCmd_Unlock | Input | BOOL | CmdSrc.PCmd_Unlock | 0 | Decimal | 0 | 0 | Program command to unlock Program (allow Operator to acquire). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_Acq | Input | BOOL | CmdSrc.XCmd_Acq | 0 | Decimal | 0 | 0 | External command to acquire ownership (Operator/Program/Override/Maintenance to External). The instruction clears this operand automatically if Cfg_ExtAcqAsLevel = 0. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_Rel | Input | BOOL | CmdSrc.XCmd_Rel | 0 | Decimal | 0 | 0 | External command to release ownership if Cfg_ExtAcqAsLevel = 0 (External to Operator/Program/Override/Maintenance). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_OwnerAcq | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to acquire child command source. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_OwnerRel | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to release child command source. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_Start | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to start. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_Stop | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to stop. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_Abort | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to Abort. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_Hold | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to Hold. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_Restart | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to restart. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_Resume | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to Resume from Paused. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_Pause | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to Pause. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_AutoPause | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to Auto Pause. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_ResetPhs | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to reset phase. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_StateForce | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to force state. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_ParCapture | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to capture initial parameter. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_ParClear | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to clear parameter. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_ParRestore | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to restore initial parameter. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_RptCapture | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to capture initial report. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_RptClear | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to clear report. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_RptRestore | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to restore initial report. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to reset shed latches and cleared alarms. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_EPGen | XCmd_ResetAckAll | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to acknowledge and reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_ExtddAlm | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Opr_ExtddAlm | Inp_InitializeReq | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Request to initialize the instruction. The instruction is normally initialized in instruction first run. Use this request when reinitialization is needed. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_ExtddAlm | Inp | Input | BOOL |  | 2#0 | Binary | 0 | 0 | 1 = Alarm trigger. | Read Only | 0 | 0
raP_Opr_ExtddAlm | Inp_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset all fault conditions and latched alarms. | Read/Write | 0 | 0
raP_Opr_ExtddAlm | Inp_RdyReset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Related object, reset by this object, is ready to be reset. | Read/Write | 0 | 0
raP_Opr_ExtddAlm | PCmd_Reset | Input | BOOL |  | 0 | Decimal | 1 | 1 | Program command to reset alarm request. | Read/Write | 0 | 0
raP_Opr_ExtddAlm | PCmd_ResetAckAll | Input | BOOL |  | 0 | Decimal | 1 | 1 | Program command to reset and acknowledge all alarms. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_ExtddAlm | PCmd_Disable | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to disable alarm request. | Read/Write | 0 | 0
raP_Opr_ExtddAlm | PCmd_Enable | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to enable alarm request. | Read/Write | 0 | 0
raP_Opr_ExtddAlm | PCmd_Suppress | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to suppress alarm request. | Read/Write | 0 | 0
raP_Opr_ExtddAlm | PCmd_Unshelve | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to unshelve alarm request. | Read/Write | 0 | 0
raP_Opr_ExtddAlm | PCmd_UnSuppress | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to unsuppress alarm request. | Read/Write | 0 | 0
raP_Opr_ExtddAlm | XCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | External Command to reset shed latches and cleared alarms. | Read/Write | 0 | 0
raP_Opr_ExtddAlm | XCmd_ResetAckAll | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to acknowledge and reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_OrgScan | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Opr_OrgScan | Inp_InitializeReq | Input | BOOL |  | 0 | Decimal | 0 | 0 | Request to Initialize. | Read/Write | 0 | 0
raP_Opr_OrgScan | Inp_NodeSelected | Input | DINT |  | 0 | Decimal | 0 | 0 | Input to select the Node array index for edit. | Read/Write | 0 | 0
raP_Opr_OrgScan | Inp_BusSelected | Input | DINT |  | 0 | Decimal | 0 | 0 | Input to select the Bus array index for edit. | Read/Write | 0 | 0
raP_Opr_OrgScan | OCmd_AddChild | Input | BOOL |  | 0 | Decimal | 0 | 0 | Operator command to add a child to a node. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_OrgScan | OCmd_DelNode | Input | BOOL |  | 0 | Decimal | 0 | 0 | Operator command to delete a node. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_OrgScan | OCmd_SetBus | Input | BOOL |  | 0 | Decimal | 0 | 0 | Operator command to assign a Bus index to a Node. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_OrgScan | OSet_EOwner | Input | DINT | Own.OSet_Owner | 0 | Decimal | 0 | 0 | Operator Owner Request by ID. | None | 0 | 0
raP_Opr_OrgScan | PSet_EOwner | Input | DINT | Own.PSet_Owner | 0 | Decimal | 0 | 0 | Program Owner Request by ID. | None | 0 | 0
raP_Opr_OrgScan | XSet_EOwner | Input | DINT | Own.XSet_Owner | 0 | Decimal | 0 | 0 | External Owner Request by ID. | None | 0 | 0
raP_Opr_OrgScan | MSet_EOwner | Input | DINT | Own.MSet_Owner | 0 | Decimal | 0 | 0 | Maintenance Owner Requst by ID. | None | 0 | 0
raP_Opr_OrgScan | Val_EOwner | Input | DINT | Own.Val_Owner | 0 | Decimal | 0 | 0 | ID of the current dominant owner. | None | 0 | 0
raP_Opr_OrgView | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Opr_OrgView | Inp_InitReq | Input | BOOL |  | 0 | Decimal | 0 | 0 | Request to Initialize. | Read/Write | 0 | 0
raP_Opr_OrgView | Cfg_EditEN | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = allow this client to edit the organizaion. | Read/Write | 0 | 0
raP_Opr_OrgView | Cmd_EditReq | Input | BOOL |  | 0 | Decimal | 0 | 0 | Command: request to become the organization editor. This instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_OrgView | Set_FindBusObj | Input | INT |  | 0 | Decimal | 0 | 0 | Bus index of object to find. | Read/Write | 0 | 0
raP_Opr_Owner | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Opr_Owner | Inp_InitializeReq | Input | BOOL |  | 0 | Decimal | 0 | 0 | Request to initialize. | Read/Write | 0 | 0
raP_Opr_Owner | Inp_ChildrenOwned | Input | BOOL |  | 1 | Decimal | 0 | 0 | Input to confirm child state and ownership. | Read/Write | 0 | 0
raP_Opr_Owner | Inp_ChildrenOrganized | Input | BOOL |  | 1 | Decimal | 0 | 0 | Input to confirm child state and ownership. | Read/Write | 0 | 0
raP_Opr_Owner | Inp_NotRdy | Input | BOOL |  | 0 | Decimal | 0 | 0 | Input to confirm NotRdy status of children. | Read/Write | 0 | 0
raP_Opr_Owner | Inp_OArbOwner | Input | DINT |  | 0 | Decimal | 0 | 0 | Input for optional Arbitration Operator owner requests. | Read/Write | 0 | 0
raP_Opr_Owner | Inp_PArbOwner | Input | DINT |  | 0 | Decimal | 0 | 0 | Input for optional Arbitration Program owner requests. | Read/Write | 0 | 0
raP_Opr_Owner | Inp_XArbOwner | Input | DINT |  | 0 | Decimal | 0 | 0 | Input for optional Arbitration External owner requests. | Read/Write | 0 | 0
raP_Opr_Owner | Inp_MArbOwner | Input | DINT |  | 0 | Decimal | 0 | 0 | Input for optional Arbitration Maintenance owner requests. | Read/Write | 0 | 0
raP_Opr_Owner | Inp_OwnerSts | Input | DINT |  | 0 | Decimal | 0 | 0 | Input for associated CmdSrc status and configuration. | Read Only | 0 | 0
raP_Opr_Owner | Cfg_OperByClass | Input | BOOL |  | 0 | Decimal | 0 | 0 | Configuration to allow multiple Operator owners to transfer ownershiip. | Read/Write | 0 | 0
raP_Opr_Owner | Cfg_ProgByClass | Input | BOOL |  | 0 | Decimal | 0 | 0 | Configuration to allow multiple Program owners to transfer ownershiip. | Read/Write | 0 | 0
raP_Opr_Owner | Cfg_ExtByClass | Input | BOOL |  | 0 | Decimal | 0 | 0 | Configuration to allow multiple External owners to transfer ownershiip. | Read/Write | 0 | 0
raP_Opr_Owner | Cfg_MaintByClass | Input | BOOL |  | 0 | Decimal | 0 | 0 | Configuration to allow multiple Maintenance owners to transfer ownershiip. | Read/Write | 0 | 0
raP_Opr_Owner | PSet_Owner | Input | DINT |  | 0 | Decimal | 0 | 1 | Program Owner Request by ID. | Read/Write | 0 | 0
raP_Opr_Owner | OSet_Owner | Input | DINT |  | 0 | Decimal | 0 | 0 | Operator Owner Request by ID. | Read/Write | 0 | 0
raP_Opr_Owner | XSet_Owner | Input | DINT |  | 0 | Decimal | 0 | 0 | External Owner Request by ID. | Read/Write | 0 | 0
raP_Opr_Owner | MSet_Owner | Input | DINT |  | 0 | Decimal | 0 | 0 | Maintenance Owner Requst by ID. | Read/Write | 0 | 0
raP_Opr_Owner | OCmd_OUnbind | Input | BOOL | xLax.0 | 0 | Decimal | 0 | 0 | 1 - Do not enforce Oper CmdSrc state when owned by Oper class | Read/Write | 0 | 0
raP_Opr_Owner | OCmd_PUnbind | Input | BOOL | xLax.1 | 0 | Decimal | 0 | 0 | 1 - Do not enforce Prog CmdSrc state when owned by Prog class | Read/Write | 0 | 0
raP_Opr_Owner | OCmd_XUnbind | Input | BOOL | xLax.2 | 0 | Decimal | 0 | 0 | 1 - Do not enforce Ext CmdSrc state when owned by Ext class | Read/Write | 0 | 0
raP_Opr_Owner | OCmd_MUnbind | Input | BOOL | xLax.3 | 0 | Decimal | 0 | 0 | 1 - Do not enforce Maint CmdSrc state when owned by Maint class | Read/Write | 0 | 0
raP_Opr_Owner | Inp_UnbindAll | Input | BOOL | xLax.4 | 0 | Decimal | 0 | 0 | 1 - Do not enforce Any CmdSrc state when owned by Any class | Read/Write | 0 | 0
raP_Opr_Owner | PSet_PUnbind | Input | BOOL | xLax.5 | 0 | Decimal | 0 | 0 | 1 - Do not enforce Prog CmdSrc state when owned by Prog class | Read/Write | 0 | 0
raP_Opr_Owner | PSet_XUnbind | Input | BOOL | xLax.6 | 0 | Decimal | 0 | 0 | 1 - Do not enforce Ext CmdSrc state when owned by Ext class | Read/Write | 0 | 0
raP_Opr_Prompt | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Opr_Prompt | Inp_Req | Input | BOOL | Prompt.Inp_Req | 0 | Decimal | 0 | 0 | Input to Enable an Operator Prompt. | Read/Write | 0 | 0
raP_Opr_Prompt | Inp_Ref | Input | DINT | Prompt.Inp_Ref | 0 | Decimal | 0 | 0 | Number of Manual Prompt Configuration in the Array to Use. | Read/Write | 0 | 0
raP_Opr_Prompt | Inp_ScalePct | Input | REAL | Prompt.Inp_ScalePct | 100 | Float | 0 | 0 | Percent By Which to Scale Configured Numeric Display Values. | Read/Write | 0 | 0
raP_Opr_Prompt | Inp_Real0 | Input | REAL | Prompt.Inp_Real0 | 0 | Float | 0 | 0 | Programmatic Real Value to Display (0). | Read/Write | 0 | 0
raP_Opr_Prompt | Inp_Real1 | Input | REAL | Prompt.Inp_Real1 | 0 | Float | 0 | 0 | Programmatic Real Value to Display (1). | Read/Write | 0 | 0
raP_Opr_Prompt | Inp_Real2 | Input | REAL | Prompt.Inp_Real2 | 0 | Float | 0 | 0 | Programmatic Real Value to Display (2). | Read/Write | 0 | 0
raP_Opr_Prompt | Inp_Real3 | Input | REAL | Prompt.Inp_Real3 | 0 | Float | 0 | 0 | Programmatic Real Value to Display (3). | Read/Write | 0 | 0
raP_Opr_Prompt | Inp_Real4 | Input | REAL | Prompt.Inp_Real4 | 0 | Float | 0 | 0 | Programmatic Real Value to Display (4). | Read/Write | 0 | 0
raP_Opr_Prompt | Inp_Real5 | Input | REAL | Prompt.Inp_Real5 | 0 | Float | 0 | 0 | Programmatic Real Value to Display (5). | Read/Write | 0 | 0
raP_Opr_Prompt | Inp_Real6 | Input | REAL | Prompt.Inp_Real6 | 0 | Float | 0 | 0 | Programmatic Real Value to Display (6). | Read/Write | 0 | 0
raP_Opr_Prompt | Inp_Real7 | Input | REAL | Prompt.Inp_Real7 | 0 | Float | 0 | 0 | Programmatic Real Value to Display (7). | Read/Write | 0 | 0
raP_Opr_Prompt | Cfg_AllowDisable | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Maintenance to disable alarms. | Read/Write | 0 | 0
raP_Opr_Prompt | Cfg_AllowShelve | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Operator to shelve alarms. | Read/Write | 0 | 0
raP_Opr_Prompt | Cfg_AlertDefeat | Input | BOOL | Prompt.Cfg_AlertDefeat | 0 | Decimal | 0 | 0 | 1 = Disables the Alert icon (orange (!) ) for standalone use. | Read/Write | 0 | 0
raP_Opr_Prompt | Cfg_HasMoreObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with more info is available. | Read/Write | 0 | 0
raP_Opr_Prompt | Cfg_LocalSelect | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Local is selected. | Read/Write | 0 | 0
raP_Opr_Prompt | Cfg_HasExtended | Input | BOOL |  | 0 | Decimal | 0 | 0 | Configuration to indicate that an extended text structure exists. | Read/Write | 0 | 0
raP_Opr_Prompt | Cfg_AlertTimeOut | Input | DINT |  | 0 | Decimal | 0 | 0 | Alert timeout in seconds. | Read/Write | 0 | 0
raP_Opr_Prompt | Cfg_CnfrmReqd | Input | SINT |  | 0 | Decimal | 0 | 0 | Operator command confirmation required. Represents the type of command confirmation required. 0 = None, 1 = Command confirmation required, 2 = Performer e-signature required, 3 = Performer and approver e-signature required. | Read/Write | 0 | 0
raP_Opr_Prompt_Core | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Opr_Prompt_Core | Inp_Req | Input | BOOL |  | 0 | Decimal | 0 | 1 | Input to Enable an Operator Prompt. | Read/Write | 0 | 0
raP_Opr_Prompt_Core | Inp_Ref | Input | DINT |  | 0 | Decimal | 0 | 1 | Number of Manual Prompt Configuration in the Array to Use. | Read/Write | 0 | 0
raP_Opr_Prompt_Core | Inp_ScalePct | Input | REAL |  | 100 | Float | 0 | 0 | Percent By Which to Scale Configured Numeric Display Values. | Read/Write | 0 | 0
raP_Opr_Prompt_Core | Inp_Real0 | Input | REAL | Inp_Real[0] | 0 | Float | 0 | 0 | Programmatic Real Value to Display (0). | Read/Write | 0 | 0
raP_Opr_Prompt_Core | Inp_Real1 | Input | REAL | Inp_Real[1] | 0 | Float | 0 | 0 | Programmatic Real Value to Display (1). | Read/Write | 0 | 0
raP_Opr_Prompt_Core | Inp_Real2 | Input | REAL | Inp_Real[2] | 0 | Float | 0 | 0 | Programmatic Real Value to Display (2). | Read/Write | 0 | 0
raP_Opr_Prompt_Core | Inp_Real3 | Input | REAL | Inp_Real[3] | 0 | Float | 0 | 0 | Programmatic Real Value to Display (3). | Read/Write | 0 | 0
raP_Opr_Prompt_Core | Inp_Real4 | Input | REAL | Inp_Real[4] | 0 | Float | 0 | 0 | Programmatic Real Value to Display (4). | Read/Write | 0 | 0
raP_Opr_Prompt_Core | Inp_Real5 | Input | REAL | Inp_Real[5] | 0 | Float | 0 | 0 | Programmatic Real Value to Display (5). | Read/Write | 0 | 0
raP_Opr_Prompt_Core | Inp_Real6 | Input | REAL | Inp_Real[6] | 0 | Float | 0 | 0 | Programmatic Real Value to Display (6). | Read/Write | 0 | 0
raP_Opr_Prompt_Core | Inp_Real7 | Input | REAL | Inp_Real[7] | 0 | Float | 0 | 0 | Programmatic Real Value to Display (7). | Read/Write | 0 | 0
raP_Opr_Prompt_Core | Cfg_AlertDefeat | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Disables the Alert icon (orange (!) ) for standalone use. | Read/Write | 0 | 0
raP_Opr_Prompt_Core | Cfg_HasMoreObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with more info is available. | Read/Write | 0 | 0
raP_Opr_Unit | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Opr_Unit | Inp_InitializeReq | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Request to initialize the instruction. The instruction is normally initialized in instruction first run. Use this request when reinitialization is needed. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_EStop | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Emergency stop input ok. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_SStop | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Software stop input ok. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_Sts | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | Reference process state (bitwise). | Read/Write | 0 | 0
raP_Opr_Unit | Inp_PermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Permissive bypassable input ok. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_NBPermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Permissive non-bypassable input ok. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_IntlkOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = By-passable interlock ok. Used to input all by-passable interlock conditions for a particular instance. This Input can be connected to an external multiplexer block (Cfg_HasIntlkObj). This input will be ignored when bypass interlocks and permissives mode is active. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_NBIntlkOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Non by-passable interlock ok. Used to input all non by-passable interlock conditions for a particular instance. This Input can be connected to an external multiplexer block (Cfg_HasIntlkObj). | Read/Write | 0 | 0
raP_Opr_Unit | Inp_IntlkAvailable | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Interlock availability ok. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_IntlkTripInh | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Inhibit interlock trip status. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_RdyReset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Related object, reset by this object, is ready to be reset. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_ExtddAlmsUsed | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Tells HMI object is connected to Inp_ExtddAlmsAlm input. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_ExtddAlmsAlm | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarms active. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_ExtddAlmsAcked | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended Alarm Acknowledge. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_Unit | Inp_ExtddAlmsAlmInh | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm is shelved, disabled or suppressed. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_Unit | Inp_ExtddAlmsDisabled | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended Alarm Disabled. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_Unit | Inp_ExtddAlmsShelved | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm shelved. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_Unit | Inp_ExtddAlmsSuppressed | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm suppressed. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_Unit | Inp_ExtddAlmsAlarmFault | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm error. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_Unit | Inp_ExtddAlmsRdyReset | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = A latched extended alarm is ready to be reset. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_Unit | Inp_ExtddAlmseNotify | Input | SINT |  | 0 | Decimal | 0 | 0 | Extended alarms status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. Highest active extended alarm value. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_ExtddAlmsDsply | Input | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Extended alarm severity value is greatest of all extended alarms active. Each bit represents an individual alarm (0 - 31). | Read/Write | 0 | 0
raP_Opr_Unit | Inp_GroupCmd1NBPermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Group command 1 permissive non-bypassable input ok. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_GroupCmd1PermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Group command 1 permissive bypassable input ok. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_GroupCmd2NBPermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Group command 2 permissive non-bypassable input ok. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_GroupCmd2PermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Group command 2 permissive bypassable input ok. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_GroupCmd3NBPermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Group command 3 permissive non-bypassable input ok. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_GroupCmd3PermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Group command 3 permissive bypassable input ok. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_GroupCmd4NBPermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Group command 4 permissive non-bypassable input ok. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_GroupCmd4PermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1 = Group command 4 permissive bypassable input ok. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset all fault conditions and latched alarms. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_ExtInh | Input | BOOL | CmdSrc.Inp_ExtInh | 0 | Decimal | 0 | 0 | 1 = Inhibit External acquisition, 0 = Allow External acquisition. | Read/Write | 0 | 0
raP_Opr_Unit | Inp_PromptRdy | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 - Associated raP_Opr_Prompt is ready | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_AllowDisable | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Allow Operator alarm disable, 0 = Disallow Operator alarm disable. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_AllowShelve | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Allow Operator alarm shelve, 0 = Disallow Operator alarm shelve. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_Class | Input | BOOL |  | 0 | Decimal | 0 | 0 | Parameter will be used to define a Class of a Unit. | Read Only | 0 | 0
raP_Opr_Unit | Cfg_HasExtddAlmObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1= Extended alarms object confirmed in system. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_ShedOnExtddAlms | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Alarm on extended alarm; 0 = Alarm only on extended Alarm. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_ShedOnChildAlarm | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Shed on child alarm or alarm UnAckd; 0 = Child alarm active or UnAckd indication only. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_ShedOnChildNotUsable | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Shed on child cannot be owned or is in a state that makes it unusable for parent; 0 = Child cannot be owned or is in a state that makes it unusable for parent indication only. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasIntlkObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI unit is connected to Inp_Intlk inputs. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasPermObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI unit is connected to Inp_Perm inputs. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasSStopCM | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Software stop propagation on the bus is available. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasSStopInp | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Software stop input is available. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasMtrl | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI level and material type are available. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasBatchObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI a batch object with more info is available. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasPrompt | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Has associated raP_Opr_Prompt. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasMoreObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with more info is available. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasGroupCmds | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI equipment phase is connected to Inp_ExtddAlms input. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasGroupSts | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = External status mapping exists. Inp_Sts is mapped to Sts. 0 = Predefined status is mapped based on standard group commands. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasGroupRdy | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = External ready mapping exists. Inp_RdyOk is mapped to Rdy. 0 = Predefined ready is mapped based on standard group commands. (0 - 3 only) | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasGroupCmd1PermObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI unit is connected to group command 1 Inp_Perm inputs and confirms the permissive is enabled in the object. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasGroupCmd2PermObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI unit is connected to group command 2 Inp_Perm inputs and confirms the permissive is enabled in the object. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasGroupCmd3PermObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI unit is connected to group command 3 Inp_Perm inputs and confirms the permissive is enabled in the object. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasGroupCmd4PermObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI unit is connected to group command 4 Inp_Perm inputs and confirms the permissive is enabled in the object. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_MntnGroupCmds | Input | SINT |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI equipment phase is connected to Inp_ExtddAlms input. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_GroupCmd1FailTime | Input | REAL |  | 60 | Float | 0 | 0 | After tripped, time to reach trip position before alarm. Valid = 0.0 to 2147483.0 seconds. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_GroupCmd2FailTime | Input | REAL |  | 60 | Float | 0 | 0 | After tripped, time to reach trip position before alarm. Valid = 0.0 to 2147483.0 seconds. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_GroupCmd3FailTime | Input | REAL |  | 60 | Float | 0 | 0 | After tripped, time to reach trip position before alarm. Valid = 0.0 to 2147483.0 seconds. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_GroupCmd4FailTime | Input | REAL |  | 60 | Float | 0 | 0 | After tripped, time to reach trip position before alarm. Valid = 0.0 to 2147483.0 seconds. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_Child2BGoodTmr | Input | DINT |  | 5 | Decimal | 0 | 0 | Time to delay Child Acquisition check status (Seconds) | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_EUMax | Input | REAL |  | 100 | Float | 0 | 0 | PV (output) maximum for scaling to EU. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_EUMin | Input | REAL |  | 0 | Float | 0 | 0 | PV (output) minimum for scaling to EU. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_CnfrmReqd | Input | SINT |  | 0 | Decimal | 0 | 0 | Operator Command Confirmation Required. Represents the type of command confirmation required. 0 = None, 1 = Command confirmation required, 2 = Performer e-signature required, 3 = Performer and approver e-signature required. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_DecPlcs | Input | SINT |  | 2 | Decimal | 0 | 0 | Number of decimal places for volume display (0 to 6). | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_OwnerCmdSrc | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Command source follows owner. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_CascadeOwn | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Children will be owned when this object is owned. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_eKeepCmds | Input | SINT |  | 0 | Decimal | 0 | 0 | Ownership of module commands (enumeration): 0 = follows CmdSrc, 1 = Operator, 2 = Program, 3 = External. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_eKeepOwnerCmds | Input | SINT |  | 2 | Decimal | 0 | 0 | Ownership of module Ownership commands (enumeration): 0 = follows CmdSrc, 1 = Operator, 2 = Program, 3 = External. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasOper | Input | BOOL | CmdSrc.Cfg_HasOper | 1 | Decimal | 0 | 0 | 1 = Operator (unlocked) exists, can be selected. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasOperLocked | Input | BOOL | CmdSrc.Cfg_HasOperLocked | 1 | Decimal | 0 | 0 | 1 = Operator locked exists, can be selected. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasProg | Input | BOOL | CmdSrc.Cfg_HasProg | 1 | Decimal | 0 | 0 | 1 = Program (unlocked) exists, can be selected. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasProgLocked | Input | BOOL | CmdSrc.Cfg_HasProgLocked | 1 | Decimal | 0 | 0 | 1 = Program locked exists, can be selected. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasExt | Input | BOOL | CmdSrc.Cfg_HasExt | 0 | Decimal | 0 | 0 | 1 = External exists, can be selected. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasMaint | Input | BOOL | CmdSrc.Cfg_HasMaint | 1 | Decimal | 0 | 0 | 1 = Maintenance exists, can be selected. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasMaintOoS | Input | BOOL | CmdSrc.Cfg_HasMaintOoS | 1 | Decimal | 0 | 0 | 1 = Maintenance Out of Service exists, can be selected. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_OvrdOverLock | Input | BOOL | CmdSrc.Cfg_OvrdOverLock | 1 | Decimal | 0 | 0 | 1 = Override supersedes Program/Operator lock, 0 = Don't Override lock. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_ExtOverLock | Input | BOOL | CmdSrc.Cfg_ExtOverLock | 0 | Decimal | 0 | 0 | 1 = External supersedes Program/Operator lock, 0 = Don't Override lock. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_ProgPwrUp | Input | BOOL | CmdSrc.Cfg_ProgPwrUp | 0 | Decimal | 0 | 0 | 1 = Power up to Program, 0 = Power up to Operator. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_ProgNormal | Input | BOOL | CmdSrc.Cfg_ProgNormal | 0 | Decimal | 0 | 0 | Normal source: 1 = Program if no requests; 0 = Operator if no requests. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_PCmdPriority | Input | BOOL | CmdSrc.Cfg_PCmdPriority | 0 | Decimal | 0 | 0 | Command priority. 1 = Program commands win, 0 = Operator commands win. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_PCmdProgAsLevel | Input | BOOL | CmdSrc.Cfg_PCmdProgAsLevel | 0 | Decimal | 0 | 0 | 1 = PCmd_Prog used as a level. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_PCmdLockAsLevel | Input | BOOL | CmdSrc.Cfg_PCmdLockAsLevel | 0 | Decimal | 0 | 0 | 1 = PCmd_Lock used as a level (1 = Lock, 0 = Unlock). | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_ExtAcqAsLevel | Input | BOOL | CmdSrc.Cfg_ExtAcqAsLevel | 0 | Decimal | 0 | 0 | 1 = XCmd_Acq used as level (1 = Acquire, 0 = Release). | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_eKeepPar | Input | SINT |  | 2 | Decimal | 0 | 0 | Ownership of parameters (enumeration): 0 = follows CmdSrc, 1 = Operator, 2 = Program, 3 = External. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasParCmds | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = This equipment module has the parameter operator commands. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_NumPars | Input | INT |  | 0 | Decimal | 0 | 0 | The equipment module may be configured to use external parameter objects. This value defines the number of parameters objects defined for use. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_eKeepRpt | Input | SINT |  | 2 | Decimal | 0 | 0 | Ownership of reports (enumeration): 0 = follows CmdSrc, 1 = Operator, 2 = Program, 3 = External. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_HasRptCmds | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = This equipment module has the report operator commands. | Read/Write | 0 | 0
raP_Opr_Unit | Cfg_NumRpts | Input | INT |  | 0 | Decimal | 0 | 0 | The equipment module may be configured to use external report objects. This value defines the number of report objects defined for use. | Read/Write | 0 | 0
raP_Opr_Unit | PSet_Actl | Input | REAL |  | 0 | Float | 0 | 0 | Program setting to set actual weight/volume/ percent level. | Read/Write | 0 | 0
raP_Opr_Unit | PSet_Mtrl | Input | INT |  | 0 | Decimal | 0 | 0 | Program setting to set material type enumeration value. | Read/Write | 0 | 0
raP_Opr_Unit | PSet_Summary | Input | INT |  | 0 | Decimal | 0 | 0 | Program setting of process summary. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd | Input | SINT |  | 2#0000_0000 | Binary | 0 | 0 | Program command to State (bitwise). | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_Physical | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to select Physical device operation (not simulated). | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_Virtual | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to select Virtual (simulated) device operation. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to reset all alarms request. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_SuppressAllAlms | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to suppress all parent and child alarms if applicable. (Bus Mask set) | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_UnSuppressAllAlms | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to unsuppress all parent and child alarms if applicable. (Bus Mask set) | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_MtrlDestinationE | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to set unit as a material destination for a East neighbor connection. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_MtrlDestinationN | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to set unit as a material destination for a North neighbor connection. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_MtrlDestinationS | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to set unit as a material destination for a South neighbor connection. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_MtrlDestinationW | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to set unit as a material destination for a West neighbor connection. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_MtrlSourceE | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to set unit as a material source for a East neighbor connection. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_MtrlSourceN | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to set unit as a material source for a North neighbor connection. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_MtrlSourceS | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to set unit as a material source for a South neighbor connection. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_MtrlSourceW | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to set unit as a material source for a West neighbor connection. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_OwnerAcq | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to acquire child command source. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_OwnerRel | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to release child command source. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_UnbindChildren | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to unbind children command source. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_Oper | Input | BOOL | CmdSrc.PCmd_Oper | 0 | Decimal | 0 | 0 | Program command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_Prog | Input | BOOL | CmdSrc.PCmd_Prog | 0 | Decimal | 0 | 0 | Program command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_Lock | Input | BOOL | CmdSrc.PCmd_Lock | 0 | Decimal | 0 | 0 | Program command to lock Program (disallow Operator). The instruction clears this operand automatically if Cfg_PCmdLockAsLevel = 0. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_Unlock | Input | BOOL | CmdSrc.PCmd_Unlock | 0 | Decimal | 0 | 0 | Program command to unlock Program (allow Operator to acquire). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_Normal | Input | BOOL | CmdSrc.PCmd_Normal | 0 | Decimal | 0 | 0 | Program command to select normal command source (Operator or Program). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_ParCapture | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to capture initial parameter. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_ParClear | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to clear parameter. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_ParRestore | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to restore initial parameter. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_RptCapture | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to capture initial report. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_RptClear | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to clear report. | Read/Write | 0 | 0
raP_Opr_Unit | PCmd_RptRestore | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to restore initial report. | Read/Write | 0 | 0
raP_Opr_Unit | XCmd_Acq | Input | BOOL | CmdSrc.XCmd_Acq | 0 | Decimal | 0 | 0 | External command to acquire ownership (Operator/Program/Override/Maintenance to External). The instruction clears this operand automatically if Cfg_ExtAcqAsLevel = 0. | Read/Write | 0 | 0
raP_Opr_Unit | XCmd_Rel | Input | BOOL | CmdSrc.XCmd_Rel | 0 | Decimal | 0 | 0 | External command to release ownership if Cfg_ExtAcqAsLevel = 0 (External to Operator/Program/Override/Maintenance). The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Unit | XCmd_OwnerAcq | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to acquire child command source. | Read/Write | 0 | 0
raP_Opr_Unit | XCmd_OwnerRel | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to release child command source. | Read/Write | 0 | 0
raP_Opr_Unit | XCmd | Input | SINT |  | 2#0000_0000 | Binary | 0 | 0 | External command to State (bitwise). | Read/Write | 0 | 0
raP_Opr_Unit | XCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | External Command to reset shed latches and cleared alarms. | Read/Write | 0 | 0
raP_Opr_Unit | XCmd_ResetAckAll | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to acknowledge and reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Unit | XCmd_ParCapture | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to capture initial parameter. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Unit | XCmd_ParClear | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to clear parameter. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Unit | XCmd_ParRestore | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to restore initial parameter. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Unit | XCmd_RptCapture | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to capture initial report. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Unit | XCmd_RptClear | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to clear report. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Unit | XCmd_RptRestore | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to restore initial report. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Tec_HARTChanData_to_PAH | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Tec_HARTChanData_to_PAH | Inp_InitializeReq | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Request to initialize the instruction. The instruction is normally initialized in instruction first run. Use this request when reinitialization is needed. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Tec_LgxEvent | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Tec_LgxEvent | Inp_Event00 | Input | BOOL | Wrk_Inp.0 | 0 | Decimal | 0 | 1 | 1 = controller event 00 active. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_Event01 | Input | BOOL | Wrk_Inp.1 | 0 | Decimal | 0 | 1 | 1 = controller event 01 active. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_Event02 | Input | BOOL | Wrk_Inp.2 | 0 | Decimal | 0 | 1 | 1 = controller event 02 active. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_Event03 | Input | BOOL | Wrk_Inp.3 | 0 | Decimal | 0 | 1 | 1 = controller event 03 active. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_Event04 | Input | BOOL | Wrk_Inp.4 | 0 | Decimal | 0 | 1 | 1 = controller event 04 active. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_Event05 | Input | BOOL | Wrk_Inp.5 | 0 | Decimal | 0 | 1 | 1 = controller event 05 active. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_Event06 | Input | BOOL | Wrk_Inp.6 | 0 | Decimal | 0 | 1 | 1 = controller event 06 active. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_Event07 | Input | BOOL | Wrk_Inp.7 | 0 | Decimal | 0 | 1 | 1 = controller event 07 active. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_Event08 | Input | BOOL | Wrk_Inp.8 | 0 | Decimal | 0 | 1 | 1 = controller event 08 active. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_Event09 | Input | BOOL | Wrk_Inp.9 | 0 | Decimal | 0 | 1 | 1 = controller event 09 active. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_Event10 | Input | BOOL | Wrk_Inp.10 | 0 | Decimal | 0 | 1 | 1 = controller event 10 active. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_Event11 | Input | BOOL | Wrk_Inp.11 | 0 | Decimal | 0 | 1 | 1 = controller event 11 active. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_Event12 | Input | BOOL | Wrk_Inp.12 | 0 | Decimal | 0 | 1 | 1 = controller event 12 active. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_Event13 | Input | BOOL | Wrk_Inp.13 | 0 | Decimal | 0 | 1 | 1 = controller event 13 active. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_Event14 | Input | BOOL | Wrk_Inp.14 | 0 | Decimal | 0 | 1 | 1 = controller event 14 active. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_Event15 | Input | BOOL | Wrk_Inp.15 | 0 | Decimal | 0 | 1 | 1 = controller event 15 active. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_IOFault | Input | BOOL |  | 0 | Decimal | 0 | 1 | Input register for IO fault logic. | Read/Write | 0 | 0
raP_Tec_LgxEvent | Inp_Reset | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Reset controller event reason. | Read/Write | 0 | 0
raP_Tec_ParRpt | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Tec_ParRpt | Inp_InitializeReq | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Request to initialize the instruction. The instruction is normally initialized in instruction first run. use this request when reinitialization is needed. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Tec_ParRpt | Cfg_CnfrmReqd | Input | SINT |  | 0 | Decimal | 0 | 0 | Operator command confirmation required. Represents the type of command confirmation required. 0 = None, 1 = Command confirmation required, 2 = Performer e-signature required, 3 = Performer and approver e-signature required. | Read/Write | 0 | 0
raP_Tec_ParRpt | Cfg_Has | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Display this parameter on the HMI faceplate. | Read/Write | 0 | 0
raP_Tec_ParRpt | Cfg_DecPlcs | Input | SINT |  | 2 | Decimal | 0 | 0 | Number of decimal places for display (0 to 6). | Read/Write | 0 | 0
raP_Tec_ParRpt | Cfg_LimAdjst | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Limit the amount that the parameter value can be adjusted, from the initial value. | Read/Write | 0 | 0
raP_Tec_ParRpt | Cfg_Max | Input | DINT |  | 2147483647 | Decimal | 0 | 0 | Configure parameter maximum limits. | Read/Write | 0 | 0
raP_Tec_ParRpt | Cfg_Min | Input | DINT |  | -2147483648 | Decimal | 0 | 0 | Configure parameter minimum limits. | Read/Write | 0 | 0
raP_Tec_ParRpt | Cfg_Max_R | Input | REAL |  | 3.4028e+38 | Float | 0 | 0 | Configure real parameter maximum limits. | Read/Write | 0 | 0
raP_Tec_ParRpt | Cfg_Min_R | Input | REAL |  | -3.4028e+38 | Float | 0 | 0 | Configure real parameter minimum limits. | Read/Write | 0 | 0
raP_Tec_ParRpt | Cfg_MaxAdjst | Input | DINT |  | 2147483647 | Decimal | 0 | 0 | Amount parameter value is allowed to deviate above the initial value (Val_Initial), without producing a Limit Fault (Sts_LimFault). | Read/Write | 0 | 0
raP_Tec_ParRpt | Cfg_MinAdjst | Input | DINT |  | -2147483648 | Decimal | 0 | 0 | Amount parameter value is allowed to deviate below the initial value (Val_Initial), without producing a Limit Fault (Sts_LimFault). | Read/Write | 0 | 0
raP_Tec_ParRpt | Cfg_MaxAdjst_R | Input | REAL |  | 3.4028e+38 | Float | 0 | 0 | Amount real parameter value is allowed to deviate above the initial value (Val_Initial), without producing a Limit Fault (Sts_LimFault). | Read/Write | 0 | 0
raP_Tec_ParRpt | Cfg_MinAdjst_R | Input | REAL |  | -3.4028e+38 | Float | 0 | 0 | Amount real parameter value is allowed to deviate below the initial value (Val_Initial), without producing a Limit Fault (Sts_LimFault). | Read/Write | 0 | 0
raP_Tec_ParRpt | Cfg_ReadWrite | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow read/write of setting from HMI, 0 = Setting is read only from HMI. | Read/Write | 0 | 0
raP_Tec_ParRpt | Cfg_RestrictOper | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Restrict adjustment of the parameter from the HMI faceplate, permit only when in Operator mode 0 = Allow adjustment of the parameter from the HMI regardless of mode. | Read/Write | 0 | 0
raP_Tec_ParRpt | Cfg_EnumMax | Input | SINT |  | 10 | Decimal | 0 | 0 | Enumeration parameter maximum display limit. | Read/Write | 0 | 0
raP_Opr_Seq | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Opr_Seq | Inp_Hand | Input | BOOL | CmdSrc.Inp_Hand | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Inp_Ovrd | Input | BOOL | CmdSrc.Inp_Ovrd | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Inp_PermOK | Input | BOOL | StateMachine.Inp_PermOK | 1 | Decimal | 0 | 1 | 1=Permissives OK | Read/Write | 0 | 0
raP_Opr_Seq | Inp_NBPermOK | Input | BOOL | StateMachine.Inp_NBPermOK | 1 | Decimal | 0 | 1 | 1=Non-Bypassable Permissives OK | Read/Write | 0 | 0
raP_Opr_Seq | Inp_IntlkOK | Input | BOOL | StateMachine.Inp_IntlkOK | 1 | Decimal | 0 | 1 | 1=Interlocks OK | Read/Write | 0 | 0
raP_Opr_Seq | Inp_NBIntlkOK | Input | BOOL | StateMachine.Inp_NBIntlkOK | 1 | Decimal | 0 | 1 | 1=Non-Bypassable Interlocks OK | Read/Write | 0 | 0
raP_Opr_Seq | Inp_IntlkAvailable | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Interlock availability ok. | Read/Write | 0 | 0
raP_Opr_Seq | Inp_IntlkTripInh | Input | BOOL |  | 0 | Decimal | 0 | 0 |  | Read/Write | 0 | 0
raP_Opr_Seq | Inp_ExtInh | Input | BOOL | CmdSrc.Inp_ExtInh | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Inp_Qualified | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 - Inputs are qualified | Read/Write | 0 | 0
raP_Opr_Seq | Inp_BranchQualified | Input | BOOL | Wrk_SeqCore.Inp_Branch | 0 | Decimal | 0 | 0 | 1 - take the branch for the current step | Read/Write | 0 | 0
raP_Opr_Seq | Inp_MaintByp | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 - An upstream element is in Maintenance Bypass | Read/Write | 0 | 0
raP_Opr_Seq | Inp_PromptCfm | Input | BOOL | Wrk_SeqCore.Inp_PromptCfm | 0 | Decimal | 0 | 0 | 1 - Associated raP_Opr_Prompt is confirmed | Read/Write | 0 | 0
raP_Opr_Seq | Inp_PromptRdy | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Associated raP_Opr_Prompt is ready | Read/Write | 0 | 0
raP_Opr_Seq | Inp_PromptSelect | Input | SINT | Wrk_SeqCore.Inp_PromptSelect | 0 | Decimal | 0 | 0 | Value of associated raP_Opr_Prompt selection | Read/Write | 0 | 0
raP_Opr_Seq | Inp_OwnChildren | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Ownership request for all children in the Bus organizational tree | Read/Write | 0 | 0
raP_Opr_Seq | Inp_UnBindChildren | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Child Prog State Will Not Be Enforced When Owned | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_InSeqTimeOut | Input | DINT |  | 0 | Decimal | 0 | 0 | Sequence timeout configuration (Sec) | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_Child2BGoodTmr | Input | DINT |  | 5 | Decimal | 0 | 0 | Time to delay Child Acquisition check status (Seconds) | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_QtyMin | Input | INT |  | 0 | Decimal | 0 | 0 | Quantity Input Lower Limit | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_QtyMax | Input | INT |  | 100 | Decimal | 0 | 0 | Quantity Input Upper Limit | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_StdQty | Input | INT |  | 100 | Decimal | 0 | 0 | Quantity Input Standard (Nominal) Value (=100%) | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_CnfrmReqd | Input | SINT |  | 0 | Decimal | 0 | 0 | Operator Command Confirmation Required. Represents the type of command confirmation required. 0 = None, 1 = Command confirmation required, 2 = Performer e-signature required, 3 = Performer and approver e-signature required. | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_CascadeOwn | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Children will be owned when this object is owned. | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasOper | Input | BOOL | CmdSrc.Cfg_HasOper | 1 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasOperLocked | Input | BOOL | CmdSrc.Cfg_HasOperLocked | 1 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasProg | Input | BOOL | CmdSrc.Cfg_HasProg | 1 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasProgLocked | Input | BOOL | CmdSrc.Cfg_HasProgLocked | 1 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasExt | Input | BOOL | CmdSrc.Cfg_HasExt | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasMaint | Input | BOOL | CmdSrc.Cfg_HasMaint | 1 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasMaintOoS | Input | BOOL | CmdSrc.Cfg_HasMaintOoS | 1 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_OvrdOverLock | Input | BOOL | CmdSrc.Cfg_OvrdOverLock | 1 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_ExtOverLock | Input | BOOL | CmdSrc.Cfg_ExtOverLock | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_ProgPwrUp | Input | BOOL | CmdSrc.Cfg_ProgPwrUp | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_ProgNormal | Input | BOOL | CmdSrc.Cfg_ProgNormal | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_PCmdPriority | Input | BOOL | CmdSrc.Cfg_PCmdPriority | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_PCmdProgAsLevel | Input | BOOL | CmdSrc.Cfg_PCmdProgAsLevel | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_PCmdLockAsLevel | Input | BOOL | CmdSrc.Cfg_PCmdLockAsLevel | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_ExtAcqAsLevel | Input | BOOL | CmdSrc.Cfg_ExtAcqAsLevel | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasStartRun | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Start command in Running | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasStartStopd | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Start command in Stopped | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasAbortStopd | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Abort command in Stopped | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasSuspend | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Has Suspend/Suspended/Unsuspending | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasComplete | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Has Complete command | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasHold | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = States Holding Held Restarting are available in the HMI | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasStop | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = States Stopping Stopped are available in the HMI | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasAbort | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = States Aborting Aborted are available in the HMI | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasClear | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Has Clear command | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasPermObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an permissive object (for example, P_Perm) is used for Inp_PermOK and navigation to the permissive objects faceplate is enabled. Important: The name of the permissive object in the controller must be this raP_Opr_Seq objects name with the suffix _Perm | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasIntlkObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an interlock object (for example, P_Intlk) is used for Inp_IntlkOK and navigation to the interlock objects faceplate is enabled. Important: The name of the interlock object in the controller must be this raP_Opr_Seq objects name with the suffix _Intlk | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasScaling | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Has Real Output Value Scaling | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasMoreObj | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tells HMI an object with more info is available. | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_AllowDisable | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Maintenance to disable alarms. | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_AllowShelve | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Allow Operator to shelve alarms. | Read/Write | 0 | 0
raP_Opr_Seq | Cfg_HasPrompt | Input | BOOL | Wrk_SeqCore.Cfg_HasPrompt | 0 | Decimal | 0 | 0 | 1 - Has associated raP_Opr_Prompt | Read/Write | 0 | 0
raP_Opr_Seq | PSet_Owner | Input | DINT |  | 0 | Decimal | 0 | 0 | Program Owner Request ID (non-zero) or Release (zero) | Read/Write | 0 | 0
raP_Opr_Seq | PSet_Qty | Input | INT |  | 100 | Decimal | 0 | 0 | Program Quantity Input Value | Read/Write | 0 | 0
raP_Opr_Seq | XSet_Qty | Input | INT |  | 100 | Decimal | 0 | 0 | External Quantity Input Value | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to reset all alarms requiring reset. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_ResetAckAll | Input | BOOL |  | 0 | Decimal | 0 | 0 | Program command to reset and acknowlege all alarms requiring reset. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Seq | XCmd_Reset | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to reset all alarms requiring reset. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Seq | XCmd_ResetAckAll | Input | BOOL |  | 0 | Decimal | 0 | 0 | External command to reset and acknowlege all alarms requiring reset. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_SeqStart | Input | BOOL | StateMachine.PCmd.0 | 0 | Decimal | 0 | 0 | Start | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_SeqComplete | Input | BOOL | StateMachine.PCmd.5 | 0 | Decimal | 0 | 0 | Complete | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_SeqSuspend | Input | BOOL | StateMachine.PCmd.3 | 0 | Decimal | 0 | 0 | Suspend | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_SeqUnSuspend | Input | BOOL | StateMachine.PCmd.4 | 0 | Decimal | 0 | 0 | Unsuspend | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_SeqHold | Input | BOOL | StateMachine.PCmd.6 | 0 | Decimal | 0 | 0 | Hold | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_SeqRestart | Input | BOOL | StateMachine.PCmd.7 | 0 | Decimal | 0 | 0 | Restart | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_SeqStop | Input | BOOL | StateMachine.PCmd.8 | 0 | Decimal | 0 | 0 | Stop | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_SeqAbort | Input | BOOL | StateMachine.PCmd.9 | 0 | Decimal | 0 | 0 | Abort | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_SeqClear | Input | BOOL | StateMachine.PCmd.2 | 0 | Decimal | 0 | 0 | Clear | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_SeqReset | Input | BOOL | StateMachine.PCmd.1 | 0 | Decimal | 0 | 0 | Reset | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_Prog | Input | BOOL | CmdSrc.PCmd_Prog | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_Oper | Input | BOOL | CmdSrc.PCmd_Oper | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_Lock | Input | BOOL | CmdSrc.PCmd_Lock | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_Unlock | Input | BOOL | CmdSrc.PCmd_Unlock | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | PCmd_Normal | Input | BOOL | CmdSrc.PCmd_Normal | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | XCmd_SeqStart | Input | BOOL | StateMachine.XCmd.0 | 0 | Decimal | 0 | 0 | Start | Read/Write | 0 | 0
raP_Opr_Seq | XCmd_SeqComplete | Input | BOOL | StateMachine.XCmd.5 | 0 | Decimal | 0 | 0 | Complete | Read/Write | 0 | 0
raP_Opr_Seq | XCmd_SeqSuspend | Input | BOOL | StateMachine.XCmd.3 | 0 | Decimal | 0 | 0 | Suspend | Read/Write | 0 | 0
raP_Opr_Seq | XCmd_SeqUnSuspend | Input | BOOL | StateMachine.XCmd.4 | 0 | Decimal | 0 | 0 | Unsuspend | Read/Write | 0 | 0
raP_Opr_Seq | XCmd_SeqHold | Input | BOOL | StateMachine.XCmd.6 | 0 | Decimal | 0 | 0 | Hold | Read/Write | 0 | 0
raP_Opr_Seq | XCmd_SeqRestart | Input | BOOL | StateMachine.XCmd.7 | 0 | Decimal | 0 | 0 | Restart | Read/Write | 0 | 0
raP_Opr_Seq | XCmd_SeqStop | Input | BOOL | StateMachine.XCmd.8 | 0 | Decimal | 0 | 0 | Stop | Read/Write | 0 | 0
raP_Opr_Seq | XCmd_SeqAbort | Input | BOOL | StateMachine.XCmd.9 | 0 | Decimal | 0 | 0 | Abort | Read/Write | 0 | 0
raP_Opr_Seq | XCmd_SeqClear | Input | BOOL | StateMachine.XCmd.2 | 0 | Decimal | 0 | 0 | Clear | Read/Write | 0 | 0
raP_Opr_Seq | XCmd_SeqReset | Input | BOOL | StateMachine.XCmd.1 | 0 | Decimal | 0 | 0 | Reset | Read/Write | 0 | 0
raP_Opr_Seq | MCmd_Rel | Input | BOOL | CmdSrc.MCmd_Rel | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | XCmd_Acq | Input | BOOL | CmdSrc.XCmd_Acq | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | XCmd_Rel | Input | BOOL | CmdSrc.XCmd_Rel | 0 | Decimal | 0 | 0 | Command Source | Read/Write | 0 | 0
raP_Opr_Seq | Set_EditState | Input | SINT | Wrk_SeqEdit.Set_EditState | 0 | Decimal | 0 | 0 | Set the State Number to edit | Read/Write | 0 | 0
raP_Opr_Seq | Set_EditStepRel | Input | INT | Wrk_SeqEdit.Set_EditStepRel | 0 | Decimal | 0 | 0 | Set the Step Number Relative to the State to edit | Read/Write | 0 | 0
raP_Opr_Seq | Inp_EditEnable | Input | BOOL | Wrk_SeqEdit.Inp_EditEnable | 0 | Decimal | 0 | 0 | 1 - Editing is enabled | Read/Write | 0 | 0
raP_Opr_Seq | Cmd_StepAdd | Input | BOOL | Wrk_SeqEdit.Cmd_StepAdd | 0 | Decimal | 0 | 0 | Command to add a step | Read/Write | 0 | 0
raP_Opr_Seq | Cmd_StepIns | Input | BOOL | Wrk_SeqEdit.Cmd_StepIns | 0 | Decimal | 0 | 0 | Command to insert a step | Read/Write | 0 | 0
raP_Opr_Seq | Cmd_StepDel | Input | BOOL | Wrk_SeqEdit.Cmd_StepDel | 0 | Decimal | 0 | 0 | Command to delete a step | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Opr_SeqBoolInp | Inp_StepAbs | Input | DINT |  | 0 | Decimal | 0 | 1 | Numeric input of the current step number | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_0_00 | Input | BOOL | Wrk_Inputs[0].0 | 0 | Decimal | 0 | 1 | Bank 0 Input 0 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_0_01 | Input | BOOL | Wrk_Inputs[0].1 | 0 | Decimal | 0 | 1 | Bank 0 Input 1 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_0_02 | Input | BOOL | Wrk_Inputs[0].2 | 0 | Decimal | 0 | 1 | Bank 0 Input 2 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_0_03 | Input | BOOL | Wrk_Inputs[0].3 | 0 | Decimal | 0 | 1 | Bank 0 Input 3 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_0_04 | Input | BOOL | Wrk_Inputs[0].4 | 0 | Decimal | 0 | 1 | Bank 0 Input 4 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_0_05 | Input | BOOL | Wrk_Inputs[0].5 | 0 | Decimal | 0 | 1 | Bank 0 Input 5 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_0_06 | Input | BOOL | Wrk_Inputs[0].6 | 0 | Decimal | 0 | 1 | Bank 0 Input 6 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_0_07 | Input | BOOL | Wrk_Inputs[0].7 | 0 | Decimal | 0 | 1 | Bank 0 Input 7 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_0_08 | Input | BOOL | Wrk_Inputs[0].8 | 0 | Decimal | 0 | 1 | Bank 0 Input 8 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_0_09 | Input | BOOL | Wrk_Inputs[0].9 | 0 | Decimal | 0 | 0 | Bank 0 Input 9 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_0_10 | Input | BOOL | Wrk_Inputs[0].10 | 0 | Decimal | 0 | 0 | Bank 0 Input 10 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_0_11 | Input | BOOL | Wrk_Inputs[0].11 | 0 | Decimal | 0 | 0 | Bank 0 Input 11 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_0_12 | Input | BOOL | Wrk_Inputs[0].12 | 0 | Decimal | 0 | 0 | Bank 0 Input 12 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_0_13 | Input | BOOL | Wrk_Inputs[0].13 | 0 | Decimal | 0 | 0 | Bank 0 Input 13 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_0_14 | Input | BOOL | Wrk_Inputs[0].14 | 0 | Decimal | 0 | 0 | Bank 0 Input 14 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_0_15 | Input | BOOL | Wrk_Inputs[0].15 | 0 | Decimal | 0 | 0 | Bank 0 Input 15 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_1_00 | Input | BOOL | Wrk_Inputs[1].0 | 0 | Decimal | 0 | 0 | Bank 1 Input 0 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_1_01 | Input | BOOL | Wrk_Inputs[1].1 | 0 | Decimal | 0 | 0 | Bank 1 Input 1 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_1_02 | Input | BOOL | Wrk_Inputs[1].2 | 0 | Decimal | 0 | 0 | Bank 1 Input 2 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_1_03 | Input | BOOL | Wrk_Inputs[1].3 | 0 | Decimal | 0 | 0 | Bank 1 Input 3 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_1_04 | Input | BOOL | Wrk_Inputs[1].4 | 0 | Decimal | 0 | 0 | Bank 1 Input 4 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_1_05 | Input | BOOL | Wrk_Inputs[1].5 | 0 | Decimal | 0 | 0 | Bank 1 Input 5 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_1_06 | Input | BOOL | Wrk_Inputs[1].6 | 0 | Decimal | 0 | 0 | Bank 1 Input 6 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_1_07 | Input | BOOL | Wrk_Inputs[1].7 | 0 | Decimal | 0 | 0 | Bank 1 Input 7 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_1_08 | Input | BOOL | Wrk_Inputs[1].8 | 0 | Decimal | 0 | 0 | Bank 1 Input 8 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_1_09 | Input | BOOL | Wrk_Inputs[1].9 | 0 | Decimal | 0 | 0 | Bank 1 Input 9 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_1_10 | Input | BOOL | Wrk_Inputs[1].10 | 0 | Decimal | 0 | 0 | Bank 1 Input 10 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_1_11 | Input | BOOL | Wrk_Inputs[1].11 | 0 | Decimal | 0 | 0 | Bank 1 Input 11 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_1_12 | Input | BOOL | Wrk_Inputs[1].12 | 0 | Decimal | 0 | 0 | Bank 1 Input 12 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_1_13 | Input | BOOL | Wrk_Inputs[1].13 | 0 | Decimal | 0 | 0 | Bank 1 Input 13 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_1_14 | Input | BOOL | Wrk_Inputs[1].14 | 0 | Decimal | 0 | 0 | Bank 1 Input 14 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_1_15 | Input | BOOL | Wrk_Inputs[1].15 | 0 | Decimal | 0 | 0 | Bank 1 Input 15 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_2_00 | Input | BOOL | Wrk_Inputs[2].00 | 0 | Decimal | 0 | 0 | Bank 2 Input 0 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_2_01 | Input | BOOL | Wrk_Inputs[2].01 | 0 | Decimal | 0 | 0 | Bank 2 Input 1 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_2_02 | Input | BOOL | Wrk_Inputs[2].02 | 0 | Decimal | 0 | 0 | Bank 2 Input 2 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_2_03 | Input | BOOL | Wrk_Inputs[2].03 | 0 | Decimal | 0 | 0 | Bank 2 Input 3 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_2_04 | Input | BOOL | Wrk_Inputs[2].04 | 0 | Decimal | 0 | 0 | Bank 2 Input 4 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_2_05 | Input | BOOL | Wrk_Inputs[2].05 | 0 | Decimal | 0 | 0 | Bank 2 Input 5 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_2_06 | Input | BOOL | Wrk_Inputs[2].06 | 0 | Decimal | 0 | 0 | Bank 2 Input 6 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_2_07 | Input | BOOL | Wrk_Inputs[2].07 | 0 | Decimal | 0 | 0 | Bank 2 Input 7 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_2_08 | Input | BOOL | Wrk_Inputs[2].08 | 0 | Decimal | 0 | 0 | Bank 2 Input 8 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_2_09 | Input | BOOL | Wrk_Inputs[2].09 | 0 | Decimal | 0 | 0 | Bank 2 Input 9 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_2_10 | Input | BOOL | Wrk_Inputs[2].10 | 0 | Decimal | 0 | 0 | Bank 2 Input 10 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_2_11 | Input | BOOL | Wrk_Inputs[2].11 | 0 | Decimal | 0 | 0 | Bank 2 Input 11 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_2_12 | Input | BOOL | Wrk_Inputs[2].12 | 0 | Decimal | 0 | 0 | Bank 2 Input 12 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_2_13 | Input | BOOL | Wrk_Inputs[2].13 | 0 | Decimal | 0 | 0 | Bank 2 Input 13 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_2_14 | Input | BOOL | Wrk_Inputs[2].14 | 0 | Decimal | 0 | 0 | Bank 2 Input 14 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_2_15 | Input | BOOL | Wrk_Inputs[2].15 | 0 | Decimal | 0 | 0 | Bank 2 Input 15 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_3_00 | Input | BOOL | Wrk_Inputs[3].00 | 0 | Decimal | 0 | 0 | Bank 3 Input 0 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_3_01 | Input | BOOL | Wrk_Inputs[3].01 | 0 | Decimal | 0 | 0 | Bank 3 Input 1 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_3_02 | Input | BOOL | Wrk_Inputs[3].02 | 0 | Decimal | 0 | 0 | Bank 3 Input 2 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_3_03 | Input | BOOL | Wrk_Inputs[3].03 | 0 | Decimal | 0 | 0 | Bank 3 Input 3 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_3_04 | Input | BOOL | Wrk_Inputs[3].04 | 0 | Decimal | 0 | 0 | Bank 3 Input 4 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_3_05 | Input | BOOL | Wrk_Inputs[3].05 | 0 | Decimal | 0 | 0 | Bank 3 Input 5 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_3_06 | Input | BOOL | Wrk_Inputs[3].06 | 0 | Decimal | 0 | 0 | Bank 3 Input 6 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_3_07 | Input | BOOL | Wrk_Inputs[3].07 | 0 | Decimal | 0 | 0 | Bank 3 Input 7 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_3_08 | Input | BOOL | Wrk_Inputs[3].08 | 0 | Decimal | 0 | 0 | Bank 3 Input 8 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_3_09 | Input | BOOL | Wrk_Inputs[3].09 | 0 | Decimal | 0 | 0 | Bank 3 Input 9 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_3_10 | Input | BOOL | Wrk_Inputs[3].10 | 0 | Decimal | 0 | 0 | Bank 3 Input 10 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_3_11 | Input | BOOL | Wrk_Inputs[3].11 | 0 | Decimal | 0 | 0 | Bank 3 Input 11 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_3_12 | Input | BOOL | Wrk_Inputs[3].12 | 0 | Decimal | 0 | 0 | Bank 3 Input 12 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_3_13 | Input | BOOL | Wrk_Inputs[3].13 | 0 | Decimal | 0 | 0 | Bank 3 Input 13 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_3_14 | Input | BOOL | Wrk_Inputs[3].14 | 0 | Decimal | 0 | 0 | Bank 3 Input 14 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_3_15 | Input | BOOL | Wrk_Inputs[3].15 | 0 | Decimal | 0 | 0 | Bank 3 Input 15 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_4_00 | Input | BOOL | Wrk_Inputs[4].00 | 0 | Decimal | 0 | 0 | Bank 4 Input 0 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_4_01 | Input | BOOL | Wrk_Inputs[4].01 | 0 | Decimal | 0 | 0 | Bank 4 Input 1 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_4_02 | Input | BOOL | Wrk_Inputs[4].02 | 0 | Decimal | 0 | 0 | Bank 4 Input 2 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_4_03 | Input | BOOL | Wrk_Inputs[4].03 | 0 | Decimal | 0 | 0 | Bank 4 Input 3 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_4_04 | Input | BOOL | Wrk_Inputs[4].04 | 0 | Decimal | 0 | 0 | Bank 4 Input 4 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_4_05 | Input | BOOL | Wrk_Inputs[4].05 | 0 | Decimal | 0 | 0 | Bank 4 Input 5 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_4_06 | Input | BOOL | Wrk_Inputs[4].06 | 0 | Decimal | 0 | 0 | Bank 4 Input 6 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_4_07 | Input | BOOL | Wrk_Inputs[4].07 | 0 | Decimal | 0 | 0 | Bank 4 Input 7 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_4_08 | Input | BOOL | Wrk_Inputs[4].08 | 0 | Decimal | 0 | 0 | Bank 4 Input 8 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_4_09 | Input | BOOL | Wrk_Inputs[4].09 | 0 | Decimal | 0 | 0 | Bank 4 Input 9 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_4_10 | Input | BOOL | Wrk_Inputs[4].10 | 0 | Decimal | 0 | 0 | Bank 4 Input 10 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_4_11 | Input | BOOL | Wrk_Inputs[4].11 | 0 | Decimal | 0 | 0 | Bank 4 Input 11 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_4_12 | Input | BOOL | Wrk_Inputs[4].12 | 0 | Decimal | 0 | 0 | Bank 4 Input 12 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_4_13 | Input | BOOL | Wrk_Inputs[4].13 | 0 | Decimal | 0 | 0 | Bank 4 Input 13 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_4_14 | Input | BOOL | Wrk_Inputs[4].14 | 0 | Decimal | 0 | 0 | Bank 4 Input 14 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_4_15 | Input | BOOL | Wrk_Inputs[4].15 | 0 | Decimal | 0 | 0 | Bank 4 Input 15 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_5_00 | Input | BOOL | Wrk_Inputs[5].00 | 0 | Decimal | 0 | 0 | Bank 5 Input 0 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_5_01 | Input | BOOL | Wrk_Inputs[5].01 | 0 | Decimal | 0 | 0 | Bank 5 Input 1 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_5_02 | Input | BOOL | Wrk_Inputs[5].02 | 0 | Decimal | 0 | 0 | Bank 5 Input 2 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_5_03 | Input | BOOL | Wrk_Inputs[5].03 | 0 | Decimal | 0 | 0 | Bank 5 Input 3 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_5_04 | Input | BOOL | Wrk_Inputs[5].04 | 0 | Decimal | 0 | 0 | Bank 5 Input 4 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_5_05 | Input | BOOL | Wrk_Inputs[5].05 | 0 | Decimal | 0 | 0 | Bank 5 Input 5 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_5_06 | Input | BOOL | Wrk_Inputs[5].06 | 0 | Decimal | 0 | 0 | Bank 5 Input 6 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_5_07 | Input | BOOL | Wrk_Inputs[5].07 | 0 | Decimal | 0 | 0 | Bank 5 Input 7 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_5_08 | Input | BOOL | Wrk_Inputs[5].08 | 0 | Decimal | 0 | 0 | Bank 5 Input 8 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_5_09 | Input | BOOL | Wrk_Inputs[5].09 | 0 | Decimal | 0 | 0 | Bank 5 Input 9 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_5_10 | Input | BOOL | Wrk_Inputs[5].10 | 0 | Decimal | 0 | 0 | Bank 5 Input 10 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_5_11 | Input | BOOL | Wrk_Inputs[5].11 | 0 | Decimal | 0 | 0 | Bank 5 Input 11 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_5_12 | Input | BOOL | Wrk_Inputs[5].12 | 0 | Decimal | 0 | 0 | Bank 5 Input 12 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_5_13 | Input | BOOL | Wrk_Inputs[5].13 | 0 | Decimal | 0 | 0 | Bank 5 Input 13 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_5_14 | Input | BOOL | Wrk_Inputs[5].14 | 0 | Decimal | 0 | 0 | Bank 5 Input 14 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_5_15 | Input | BOOL | Wrk_Inputs[5].15 | 0 | Decimal | 0 | 0 | Bank 5 Input 15 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_6_00 | Input | BOOL | Wrk_Inputs[6].00 | 0 | Decimal | 0 | 0 | Bank 6 Input 0 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_6_01 | Input | BOOL | Wrk_Inputs[6].01 | 0 | Decimal | 0 | 0 | Bank 6 Input 1 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_6_02 | Input | BOOL | Wrk_Inputs[6].02 | 0 | Decimal | 0 | 0 | Bank 6 Input 2 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_6_03 | Input | BOOL | Wrk_Inputs[6].03 | 0 | Decimal | 0 | 0 | Bank 6 Input 3 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_6_04 | Input | BOOL | Wrk_Inputs[6].04 | 0 | Decimal | 0 | 0 | Bank 6 Input 4 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_6_05 | Input | BOOL | Wrk_Inputs[6].05 | 0 | Decimal | 0 | 0 | Bank 6 Input 5 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_6_06 | Input | BOOL | Wrk_Inputs[6].06 | 0 | Decimal | 0 | 0 | Bank 6 Input 6 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_6_07 | Input | BOOL | Wrk_Inputs[6].07 | 0 | Decimal | 0 | 0 | Bank 6 Input 7 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_6_08 | Input | BOOL | Wrk_Inputs[6].08 | 0 | Decimal | 0 | 0 | Bank 6 Input 8 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_6_09 | Input | BOOL | Wrk_Inputs[6].09 | 0 | Decimal | 0 | 0 | Bank 6 Input 9 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_6_10 | Input | BOOL | Wrk_Inputs[6].10 | 0 | Decimal | 0 | 0 | Bank 6 Input 10 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_6_11 | Input | BOOL | Wrk_Inputs[6].11 | 0 | Decimal | 0 | 0 | Bank 6 Input 11 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_6_12 | Input | BOOL | Wrk_Inputs[6].12 | 0 | Decimal | 0 | 0 | Bank 6 Input 12 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_6_13 | Input | BOOL | Wrk_Inputs[6].13 | 0 | Decimal | 0 | 0 | Bank 6 Input 13 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_6_14 | Input | BOOL | Wrk_Inputs[6].14 | 0 | Decimal | 0 | 0 | Bank 6 Input 14 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_6_15 | Input | BOOL | Wrk_Inputs[6].15 | 0 | Decimal | 0 | 0 | Bank 6 Input 15 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_7_00 | Input | BOOL | Wrk_Inputs[7].00 | 0 | Decimal | 0 | 0 | Bank 7 Input 0 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_7_01 | Input | BOOL | Wrk_Inputs[7].01 | 0 | Decimal | 0 | 0 | Bank 7 Input 1 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_7_02 | Input | BOOL | Wrk_Inputs[7].02 | 0 | Decimal | 0 | 0 | Bank 7 Input 2 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_7_03 | Input | BOOL | Wrk_Inputs[7].03 | 0 | Decimal | 0 | 0 | Bank 7 Input 3 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_7_04 | Input | BOOL | Wrk_Inputs[7].04 | 0 | Decimal | 0 | 0 | Bank 7 Input 4 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_7_05 | Input | BOOL | Wrk_Inputs[7].05 | 0 | Decimal | 0 | 0 | Bank 7 Input 5 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_7_06 | Input | BOOL | Wrk_Inputs[7].06 | 0 | Decimal | 0 | 0 | Bank 7 Input 6 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_7_07 | Input | BOOL | Wrk_Inputs[7].07 | 0 | Decimal | 0 | 0 | Bank 7 Input 7 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_7_08 | Input | BOOL | Wrk_Inputs[7].08 | 0 | Decimal | 0 | 0 | Bank 7 Input 8 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_7_09 | Input | BOOL | Wrk_Inputs[7].09 | 0 | Decimal | 0 | 0 | Bank 7 Input 9 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_7_10 | Input | BOOL | Wrk_Inputs[7].10 | 0 | Decimal | 0 | 0 | Bank 7 Input 10 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_7_11 | Input | BOOL | Wrk_Inputs[7].11 | 0 | Decimal | 0 | 0 | Bank 7 Input 11 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_7_12 | Input | BOOL | Wrk_Inputs[7].12 | 0 | Decimal | 0 | 0 | Bank 7 Input 12 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_7_13 | Input | BOOL | Wrk_Inputs[7].13 | 0 | Decimal | 0 | 0 | Bank 7 Input 13 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_7_14 | Input | BOOL | Wrk_Inputs[7].14 | 0 | Decimal | 0 | 0 | Bank 7 Input 14 | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Inp_7_15 | Input | BOOL | Wrk_Inputs[7].15 | 0 | Decimal | 0 | 0 | Bank 7 Input 15 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Inp_StepAbs | Input | DINT |  | 0 | Decimal | 0 | 1 | Numeric input of the current step number | Read/Write | 0 | 0
raP_Opr_SeqRealOut | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Opr_SeqRealOut | Inp_StepAbs | Input | DINT |  | 0 | Decimal | 0 | 1 | Numeric input of the current step number | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_ScalePercent | Input | REAL |  | 0 | Float | 0 | 0 | Multiplier for scaled outputs. Default = 1.0 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_0_00 | Input | REAL | Wrk_Inputs[0] | 0 | Float | 0 | 0 | Optional Bank 0 Input 00 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_0_01 | Input | REAL | Wrk_Inputs[1] | 0 | Float | 0 | 0 | Optional Bank 0 Input 01 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_0_02 | Input | REAL | Wrk_Inputs[2] | 0 | Float | 0 | 0 | Optional Bank 0 Input 02 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_0_03 | Input | REAL | Wrk_Inputs[3] | 0 | Float | 0 | 0 | Optional Bank 0 Input 03 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_0_04 | Input | REAL | Wrk_Inputs[4] | 0 | Float | 0 | 0 | Optional Bank 0 Input 04 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_0_05 | Input | REAL | Wrk_Inputs[5] | 0 | Float | 0 | 0 | Optional Bank 0 Input 05 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_0_06 | Input | REAL | Wrk_Inputs[6] | 0 | Float | 0 | 0 | Optional Bank 0 Input 06 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_0_07 | Input | REAL | Wrk_Inputs[7] | 0 | Float | 0 | 0 | Optional Bank 0 Input 07 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_1_00 | Input | REAL | Wrk_Inputs[8] | 0 | Float | 0 | 0 | Optional Bank 1 Input 00 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_1_01 | Input | REAL | Wrk_Inputs[9] | 0 | Float | 0 | 0 | Optional Bank 1 Input 01 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_1_02 | Input | REAL | Wrk_Inputs[10] | 0 | Float | 0 | 0 | Optional Bank 1 Input 02 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_1_03 | Input | REAL | Wrk_Inputs[11] | 0 | Float | 0 | 0 | Optional Bank 1 Input 03 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_1_04 | Input | REAL | Wrk_Inputs[12] | 0 | Float | 0 | 0 | Optional Bank 1 Input 04 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_1_05 | Input | REAL | Wrk_Inputs[13] | 0 | Float | 0 | 0 | Optional Bank 1 Input 05 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_1_06 | Input | REAL | Wrk_Inputs[14] | 0 | Float | 0 | 0 | Optional Bank 1 Input 06 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_1_07 | Input | REAL | Wrk_Inputs[15] | 0 | Float | 0 | 0 | Optional Bank 1 Input 07 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_2_00 | Input | REAL | Wrk_Inputs[16] | 0 | Float | 0 | 0 | Optional Bank 2 Input 00 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_2_01 | Input | REAL | Wrk_Inputs[17] | 0 | Float | 0 | 0 | Optional Bank 2 Input 01 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_2_02 | Input | REAL | Wrk_Inputs[18] | 0 | Float | 0 | 0 | Optional Bank 2 Input 02 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_2_03 | Input | REAL | Wrk_Inputs[19] | 0 | Float | 0 | 0 | Optional Bank 2 Input 03 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_2_04 | Input | REAL | Wrk_Inputs[20] | 0 | Float | 0 | 0 | Optional Bank 2 Input 04 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_2_05 | Input | REAL | Wrk_Inputs[21] | 0 | Float | 0 | 0 | Optional Bank 2 Input 05 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_2_06 | Input | REAL | Wrk_Inputs[22] | 0 | Float | 0 | 0 | Optional Bank 2 Input 06 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_2_07 | Input | REAL | Wrk_Inputs[23] | 0 | Float | 0 | 0 | Optional Bank 2 Input 07 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_3_00 | Input | REAL | Wrk_Inputs[24] | 0 | Float | 0 | 0 | Optional Bank 3 Input 00 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_3_01 | Input | REAL | Wrk_Inputs[25] | 0 | Float | 0 | 0 | Optional Bank 3 Input 01 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_3_02 | Input | REAL | Wrk_Inputs[26] | 0 | Float | 0 | 0 | Optional Bank 3 Input 02 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_3_03 | Input | REAL | Wrk_Inputs[27] | 0 | Float | 0 | 0 | Optional Bank 3 Input 03 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_3_04 | Input | REAL | Wrk_Inputs[28] | 0 | Float | 0 | 0 | Optional Bank 3 Input 04 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_3_05 | Input | REAL | Wrk_Inputs[29] | 0 | Float | 0 | 0 | Optional Bank 3 Input 05 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_3_06 | Input | REAL | Wrk_Inputs[30] | 0 | Float | 0 | 0 | Optional Bank 3 Input 06 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Inp_3_07 | Input | REAL | Wrk_Inputs[31] | 0 | Float | 0 | 0 | Optional Bank 3 Input 07 | Read/Write | 0 | 0
raP_Tec_SeqCore | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Tec_SeqCore | Cfg_HasPrompt | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Has associated raP_Opr_Prompt | Read/Write | 0 | 0
raP_Tec_SeqCore | Inp_State | Input | SINT |  | 0 | Decimal | 0 | 1 | Current state numerical value (0 - 31) | Read/Write | 0 | 0
raP_Tec_SeqCore | Inp_PauseEN | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 - Pause functionality is enabled | Read/Write | 0 | 0
raP_Tec_SeqCore | Inp_InputsQualified | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1 - Inputs are qualified | Read/Write | 0 | 0
raP_Tec_SeqCore | Inp_Branch | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 - take the branch for the current step | Read/Write | 0 | 0
raP_Tec_SeqCore | Inp_PromptCfm | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Associated raP_Opr_Prompt is confirmed | Read/Write | 0 | 0
raP_Tec_SeqCore | Inp_PromptSelect | Input | SINT |  | 0 | Decimal | 0 | 0 | Value of associated raP_Opr_Prompt selection | Read/Write | 0 | 0
raP_Tec_SeqCore | OCmd_SeqPause | Input | BOOL | Wrk_PauseBits.0 | 0 | Decimal | 0 | 0 | Operator Command to Pause Sequence | Read/Write | 0 | 0
raP_Tec_SeqCore | OCmd_SeqAutoPause | Input | BOOL | Wrk_PauseBits.1 | 0 | Decimal | 0 | 0 | Operator Command to Auto-Pause Sequence | Read/Write | 0 | 0
raP_Tec_SeqCore | OCmd_SeqCancelPause | Input | BOOL | Wrk_PauseBits.2 | 0 | Decimal | 0 | 0 | Operator Command to Cancel Sequence Pause or AutoPause | Read/Write | 0 | 0
raP_Tec_SeqCore | OCmd_SeqResume | Input | BOOL | Wrk_PauseBits.7 | 0 | Decimal | 0 | 0 | Operator Command to Resume Sequence | Read/Write | 0 | 0
raP_Tec_SeqCore | MCmd_StepTimerForce | Input | BOOL |  | 0 | Decimal | 0 | 0 | Force current Step Timer to qualify | Read/Write | 0 | 0
raP_Tec_SeqCore | MCmd_SeqStepForce | Input | BOOL |  | 0 | Decimal | 0 | 0 | Force sequencer to the next step | Read/Write | 0 | 0
raP_Tec_SeqCore | MSet_SingleStep | Input | BOOL |  | 0 | Decimal | 0 | 0 | Maintenance Setting to execute Single Step only: 0 = Normal, 1 = Single Step | Read/Write | 0 | 0
raP_Tec_SeqCore | MSet_StateReset | Input | DINT | Wrk_StateReset | 0 | Decimal | 0 | 0 | State Reset Bits | Read/Write | 0 | 0
raP_Tec_SeqCore | MSet_NextStep | Input | INT |  | 0 | Decimal | 0 | 0 | Maintenance setting for the next step | Read/Write | 0 | 0
raP_Tec_SeqEdit | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Tec_SeqEdit | Set_EditState | Input | SINT | Wrk_EditState | 0 | Decimal | 0 | 0 | Set the State Number to edit | Read/Write | 0 | 0
raP_Tec_SeqEdit | Set_EditStepRel | Input | INT | Wrk_EditStepRel | 0 | Decimal | 0 | 0 | Set the Step Number Relative to the State to edit | Read/Write | 0 | 0
raP_Tec_SeqEdit | Inp_EditEnable | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Editing is enabled | Read/Write | 0 | 0
raP_Tec_SeqEdit | Cmd_StepAdd | Input | BOOL |  | 0 | Decimal | 0 | 0 | Command to add a step | Read/Write | 0 | 0
raP_Tec_SeqEdit | Cmd_StepIns | Input | BOOL |  | 0 | Decimal | 0 | 0 | Command to insert a step | Read/Write | 0 | 0
raP_Tec_SeqEdit | Cmd_StepDel | Input | BOOL |  | 0 | Decimal | 0 | 0 | Command to delete a step | Read/Write | 0 | 0
raP_Opr_VSM | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Opr_VSM | Inp_InitializeReq | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1=Request to Initialize | Read/Write | 0 | 0
raP_Opr_VSM | Inp_PermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1=Permissives OK | Read/Write | 0 | 0
raP_Opr_VSM | Inp_NBPermOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1=Non-Bypassable Permissives OK | Read/Write | 0 | 0
raP_Opr_VSM | Inp_IntlkOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1=Interlocks OK | Read/Write | 0 | 0
raP_Opr_VSM | Inp_NBIntlkOK | Input | BOOL |  | 1 | Decimal | 0 | 1 | 1=Non-Bypassable Interlocks OK | Read/Write | 0 | 0
raP_Opr_VSM | Inp_StateComplete | Input | BOOL |  | 0 | Decimal | 0 | 1 | 1=Current State is Complete | Read/Write | 0 | 0
raP_Opr_VSM | Inp_CmdAux1 | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Assert CmdAux1 | Read/Write | 0 | 0
raP_Opr_VSM | Inp_CmdAux2 | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Assert CmdAux2 | Read/Write | 0 | 0
raP_Opr_VSM | MCmd_Bypass | Input | BOOL |  | 0 | Decimal | 0 | 0 | Maintenance command to bypass all bypassable interlocks and permissives. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_VSM | MCmd_Check | Input | BOOL |  | 0 | Decimal | 0 | 0 | Maintenance command to check (not bypass) all interlocks and permissives. The instruction clears this operand automatically. | Read/Write | 0 | 0
raP_Opr_VSM | Cfg_IntlkAsPerm | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Use Intlk as Perm Condition | Read/Write | 0 | 0
raP_Opr_VSM | Cfg_StateCompleteAsEdge | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = State DN Input as Edge | Read/Write | 0 | 0
raP_Opr_VSM | Cfg_OvrdPermIntlk | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ovrd Cmd over Perm and Intlk | Read/Write | 0 | 0
raP_Opr_VSM | Cfg_CmdIntlkAsEdge | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Intlk Cmd as Edge | Read/Write | 0 | 0
raP_Opr_VSM | Cfg_CmdAux1AsEdge | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Aux Cmd 1 as Edge | Read/Write | 0 | 0
raP_Opr_VSM | Cfg_CmdAux2AsEdge | Input | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Aux Cmd 2 as Edge | Read/Write | 0 | 0
raP_Opr_VSM | Cfg_IdleStateNum | Input | SINT |  | 0 | Decimal | 0 | 0 | Configured Idle State Number (0-31) | Read/Write | 0 | 0
raP_Opr_VSM | Set_CmdIntlk | Input | SINT |  | -1 | Decimal | 0 | 0 | Command Number to issue when the Intlk trips | Read/Write | 0 | 0
raP_Opr_VSM | Set_CmdAux1 | Input | SINT |  | -1 | Decimal | 0 | 0 | Command number to issue when Inp_AuxCmd1=1 | Read/Write | 0 | 0
raP_Opr_VSM | Set_CmdAux2 | Input | SINT |  | -1 | Decimal | 0 | 0 | Command number to issue when Inp_AuxCmd2=1 | Read/Write | 0 | 0
raP_Opr_VSM | Inp_HandStateNum | Input | SINT |  | 0 | Decimal | 0 | 0 | State number input in Hand | Read/Write | 0 | 0
raP_Opr_VSM | PSet_StateNum | Input | SINT |  | 0 | Decimal | 0 | 0 | State number input in Prog | Read/Write | 0 | 0
raP_Opr_VSM | Inp_OvrdStateNum | Input | SINT |  | 0 | Decimal | 0 | 0 | State number input in Ovrd | Read/Write | 0 | 0
raP_Opr_VSM | Inp_RdyOK | Input | DINT |  | 0 | Decimal | 0 | 0 | Bit mapped input to programmatically enable individual commands | Read/Write | 0 | 0
raP_Opr_VSM | Inp_eSrc | Input | DINT |  | 0 | Decimal | 0 | 0 | .2 Hand, .3 Maint, .4 Ovrd, .5 Prog, .6 Oper, .7 OoS, .8 Ext | Read/Write | 0 | 0
raP_Opr_VSM | OCmd | Input | DINT |  | 0 | Decimal | 0 | 0 | Bit mapped Operator Commands | Read/Write | 0 | 0
raP_Opr_VSM | PCmd | Input | DINT |  | 0 | Decimal | 0 | 0 | Bit mapped Program Commands | Read/Write | 0 | 0
raP_Opr_VSM | XCmd | Input | DINT |  | 0 | Decimal | 0 | 0 | Bit mapped External Commands | Read/Write | 0 | 0
raP_Opr_VSM | Inp_OvrdCmd | Input | DINT |  | 0 | Decimal | 0 | 0 | Number of command to issue in Override | Read/Write | 0 | 0
raP_Tec_EventQLoad | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0
raP_Tec_EventQLoad | Cfg_UseControllerTime | Input | BOOL |  | 1 | Decimal | 0 | 0 | 1 = Get and use controller time each execution. | Read/Write | 0 | 0
raP_Tec_EventQUnload | EnableIn | Input | BOOL |  | 1 | Decimal | 0 | 0 | Enable Input - System Defined Parameter | Read Only | 0 | 0

## Output Parameters
Library Object | Output Parameter | Input / Output | Data Type | Alias For | Default |  |  |  | Description
raP_Dvc_D4SD | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output: The EnableOut signal is not manipulated by this instruction. Its output state always reflects EnableIn Input state. | Read Only | 0
raP_Dvc_D4SD | Out_AData | Output | BOOL |  | 0 | Decimal | 0 | 1 | Output A to device. | Read Only | 0 | 0
raP_Dvc_D4SD | Out_BData | Output | BOOL |  | 0 | Decimal | 0 | 1 | Output B to device. | Read Only | 0 | 0
raP_Dvc_D4SD | Out_CData | Output | BOOL |  | 0 | Decimal | 0 | 1 | Output C to device. | Read Only | 0 | 0
raP_Dvc_D4SD | Out_DData | Output | BOOL |  | 0 | Decimal | 0 | 1 | Output D to device. | Read Only | 0 | 0
raP_Dvc_D4SD | Out_HornData | Output | BOOL |  | 0 | Decimal | 0 | 0 | Output to sound horn prior to commanded state change. | Read Only | 0 | 0
raP_Dvc_D4SD | Out_Reset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset command has been received and accepted. | Read Only | 0 | 0
raP_Dvc_D4SD | Out_OwnerSts | Output | DINT |  | 0 | Decimal | 0 | 0 | Status of command source, owner command handshake and ready status (bitmapped): All bits off = None, .10 = Operator Lock, .11 = Operator Unlock, .12 = Program Lock, .13 = Program Unlock, .14 = Acquire Maintenance, .15 = Release Maintenance, .16 = Acquire External, .17 = Release External, .18 = Has Maintenance, .19 = External Override Lock, .20 = Has External, .21 = Has Operator, .22 = Has Operator Locked, .23 = Has Program, .24 = Has Program Locked, .29 = Echo, .30 = Not Ready. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_Initialized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Instruction is initialized. 0 = Use Inp_InitializeReq to reinitialize. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_St0 | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device confirmed in State 0. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_St1 | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device confirmed in State 1. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_St2 | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device confirmed in State 2. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_St3 | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device confirmed in State 3. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_Moving | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device not yet confirmed in commanded state. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_Horn | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Sounding horn prior to commanded state change. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_Virtual | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = The instruction treats device as virtual, acting as if controlling a working device, but the outputs are kept de-energized, 0 = The instruction operates the physical device normally. | Read Only | 0 | 0
raP_Dvc_D4SD | SrcQ_IO | Output | SINT |  | 0 | Decimal | 0 | 0 | Source and quality of primary input or output: 0=Good, live, confirmed good 1=Good, live, assumed good 2=Good, no feedback, assumed good 8=Test, virtualized 9=Test, loopback 10=Test, manually entered 16=Uncertain, live, off-spec 17=Uncertain, substituted at device or bus 18=Uncertain, substituted at instruction 19=Uncertain, using last known good 20=Uncertain, using replacement value 32=Bad, signal failure 33=Bad, channel fault 34=Bad, module or communication fault 35=Bad, invalid configuration | Read Only | 0 | 0
raP_Dvc_D4SD | SrcQ | Output | SINT |  | 0 | Decimal | 0 | 0 | Source and quality of primary value or status: 0=Good, live, confirmed good 1=Good, live, assumed good 2=Good, no feedback, assumed good 8=Test, virtualized 9=Test, loopback 10=Test, manually entered 16=Uncertain, live, off-spec 17=Uncertain, substituted at device or bus 18=Uncertain, substituted at instruction 19=Uncertain, using last known good 20=Uncertain, using replacement value 32=Bad, signal failure 33=Bad, channel fault 34=Bad, module or communication fault 35=Bad, invalid configuration | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_eFdbk | Output | SINT |  | 0 | Decimal | 0 | 0 | Device feedback: 0 = None/Moving/Unknown, 1 = State 0, 2 = State 1, 3 = State 2, 4 = State 3. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_eCmd | Output | SINT |  | 0 | Decimal | 0 | 0 | Device command: 0 = None, 1 = State 0, 2 = State 1, 3 = State 2, 4 = State 3. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_eSts | Output | SINT |  | 0 | Decimal | 0 | 0 | Device status: 0 = Powerup/Reset, 1 = State 0, 2 = State 1, 3 = State 2, 4 = State 3, 5 = Moving, 6 = Horn, 7 = Out of service. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_eFault | Output | SINT |  | 0 | Decimal | 0 | 0 | Device fault status: 0 = None, 16 = Position fail, 17 = Device fault, 32 = I/O fault, 34 = Configuration error. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_eOutState | Output | SINT |  | 0 | Decimal | 0 | 0 | State of outputs to physical device: 0 = De-energized, 1 = State 0, 2 = State 1, 3 = State 2, 4 = State 3, 5 = Horn. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_eNotify | Output | SINT |  | 0 | Decimal | 0 | 0 | Summary alarm status: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_eNotifyAll | Output | SINT |  | 0 | Decimal | 0 | 0 | Summary alarm status including related objects: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_eNotifyIOFault | Output | SINT |  | 0 | Decimal | 0 | 0 | I/O fault alarm status: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_eNotifyFail | Output | SINT |  | 0 | Decimal | 0 | 0 | Device fail alarm status: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_eNotifyIntlkTrip | Output | SINT |  | 0 | Decimal | 0 | 0 | Interlock trip alarm status: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_eNotifyEqpFault | Output | SINT |  | 0 | Decimal | 0 | 0 | Device-reported equipment fault alarm status: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_UnackAlmCount | Output | DINT |  | 0 | Decimal | 0 | 0 | Count of unacknowledged alarms. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_eSrc | Output | INT | CmdSrc.Sts_eSrc | 0 | Decimal | 0 | 0 | Current command source: 0 = Logic not in use, 4 = Hand, 8 = Maintenance, 16 = Override, 32 = Program, 33 = Program Locked, 34 = Program default (Normal), 64 = Operator, 65 = Operator Locked, 66 = Operator default (Normal), 128 = Maintenance Out of Service, 129 = Programmed Out of Service (EnableIn false), 256 = External. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_bSrc | Output | INT | CmdSrc.Sts_bSrc | 2#0000_0000_0000_0000 | Binary | 0 | 0 | Active command source selections (bitmapped, for HMI): .0 = Hand, .1 = Programmed Out of Service (EnableIn false), .2= Maintenance Out of Service, .3 = Maintenance, .4 = Override, .5 = External, .6 = Program Locked, .7 = Program (unlocked), .8 = Operator Locked, .9 = Operator (unlocked). | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_Available | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device has been acquired by Program and is ready and available for control. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_IntlkAvailable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device can be acquired by Program and is available for control when interlocks are OK. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_Bypass | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Bypassable interlocks and permissives are bypassed. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_BypActive | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Interlock/permissive bypassing is active (bypassed by command or in Maintenance command source). | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_MaintByp | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device has a maintenance bypass function active. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_NotRdy | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device not ready, see Sts_NrdyXxx detail bits for reason. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_NrdyCfgErr | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready, configuration error. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_NrdyEqpFault | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready, device-reported equipment fault, shed requires reset. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_NrdyFail | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready, device failure, shed requires reset. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_NrdyIntlk | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready, interlock not OK. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_NrdyIOFault | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready, I/O fault, shed requires reset. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_NrdyOoS | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready, device is Out of Service. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_NrdyPerm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready, permissives not OK, device is not allowed to change state. 0 = Device ready or partially ready, some permissives may be not OK, device can be commanded to at least one other state. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_NrdyPrioSt0 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready, Operator or External issued priority State 0 Command, shed requires reset. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration, see Sts_ErrXxx detail bits for reason. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_ErrAlm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration, Logix tag-based alarm settings invalid. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_ErrOutAPulseTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration, Cfg_OutAPulseTime invalid. Valid = 0.0 to 2147483.0, 0.0 = Output held continuously. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_ErrOutBPulseTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration, Cfg_OutBPulseTime invalid. Valid = 0.0 to 2147483.0, 0.0 = Output held continuously. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_ErrOutCPulseTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration, Cfg_OutCPulseTime invalid. Valid = 0.0 to 2147483.0, 0.0 = Output held continuously. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_ErrOutDPulseTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration, Cfg_OutDPulseTime invalid. Valid = 0.0 to 2147483.0, 0.0 = Output held continuously. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_ErrVirtualFdbkTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration, Cfg_VirtualFdbkTime invalid. Valid = 0.0 to 2147483.0. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_ErrFailTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration, Cfg_FailTime invalid. Valid = 0.0 to 2147483.0. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_Hand | Output | BOOL | CmdSrc.Sts_Hand | ?? | Decimal | 0 | 1 | 1 = Hand command source is selected. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_OoS | Output | BOOL | CmdSrc.Sts_OoS | ?? | Decimal | 0 | 1 | 1 = Out of Service command source is selected. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_Maint | Output | BOOL | CmdSrc.Sts_Maint | ?? | Decimal | 0 | 1 | 1 = Maintenance command source is selected. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_Ovrd | Output | BOOL | CmdSrc.Sts_Ovrd | ?? | Decimal | 0 | 1 | 1 = Override command source is selected. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_Ext | Output | BOOL | CmdSrc.Sts_Ext | ?? | Decimal | 0 | 1 | 1 = External command source is selected. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_Prog | Output | BOOL | CmdSrc.Sts_Prog | ?? | Decimal | 0 | 1 | 1 = Program (unlocked) command source is selected. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_ProgLocked | Output | BOOL | CmdSrc.Sts_ProgLocked | ?? | Decimal | 0 | 0 | 1 = Program Locked command source is selected. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_Oper | Output | BOOL | CmdSrc.Sts_Oper | ?? | Decimal | 0 | 1 | 1 = Operator (unlocked) command source is selected. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_OperLocked | Output | BOOL | CmdSrc.Sts_OperLocked | ?? | Decimal | 0 | 0 | 1 = Operator Locked command source is selected. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_ProgOperSel | Output | BOOL | CmdSrc.Sts_ProgOperSel | ?? | Decimal | 0 | 0 | Program/Operator selection (latch) state: 1 = Program, 0 = Operator. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_ProgOperLock | Output | BOOL | CmdSrc.Sts_ProgOperLock | ?? | Decimal | 0 | 1 | Program/Operator lock (latch) state: 1 = Locked, 0 = Unlocked. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_Normal | Output | BOOL | CmdSrc.Sts_Normal | ?? | Decimal | 0 | 0 | 1 = Selected command source is the normal source (Program or Operator). | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_ExtReqInh | Output | BOOL | CmdSrc.Sts_ExtReqInh | ?? | Decimal | 0 | 0 | 1 = External command source selection is inhibited, External is not available in current state. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_ProgReqInh | Output | BOOL | CmdSrc.Sts_ProgReqInh | ?? | Decimal | 0 | 0 | 1 = Program command source selection is inhibited, Program is not available in current state. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_MAcqRcvd | Output | BOOL | CmdSrc.Sts_MAcqRcvd | ?? | Decimal | 0 | 0 | 1 = Command to acquire Maintenance command source was received this scan. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_CmdConflict | Output | BOOL |  | ?? | Decimal | 0 | 0 | 1 = Conflicting commands received this scan. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_Alm | Output | BOOL |  | ?? | Decimal | 0 | 0 | 1 = An alarm is active. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_AlmInh | Output | BOOL |  | ?? | Decimal | 0 | 0 | 1 = An alarm is shelved or disabled. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_IOFault | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = I/O communication fault. There is a predefined default discrete Logix tag-based alarm for the status. Set standard configuration members of the discrete Logix tag-based alarm. Alarm elements can be accessed as follows: PD4SD_tag.@Alarms.Alm_IOFault.AlarmElement. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_Fail | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device position failure. There is a predefined default discrete Logix tag-based alarm for the status. Set standard configuration members of the discrete Logix tag-based alarm. Alarm elements can be accessed as follows: PD4SD_Tag.@Alarms.Alm_Fail.AlarmElement. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_IntlkTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Interlock trip, device was set to State 0 by an interlock not OK. There is a predefined default discrete Logix tag-based alarm for the status. Set standard configuration members of the discrete Logix tag-based alarm. Alarm elements can be accessed as follows: PD4SD_Tag.@Alarms.Alm_IntlkTrip.AlarmElement. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_EqpFault | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device-reported equipment fault. There is a predefined default discrete Logix tag-based alarm for the status. Set standard configuration members of the discrete Logix tag-based alarm. Alarm elements can be accessed as follows: PD4SD_Tag.@Alarms.Alm_EqpFault.AlarmElement. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_RdyAck | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is ready to be acknowledged. | Read Only | 0 | 0
raP_Dvc_D4SD | Sts_RdyReset | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = A latched alarm or shed condition is ready to be reset. | Read Only | 0 | 0
raP_Dvc_D4SD | XRdy_Acq | Output | BOOL | CmdSrc.XRdy_Acq | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Acq, enable button. | Read Only | 0 | 0
raP_Dvc_D4SD | XRdy_Rel | Output | BOOL | CmdSrc.XRdy_Rel | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Rel, enable button. | Read Only | 0 | 0
raP_Dvc_D4SD | XRdy_St0 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_St0, enable button. | Read Only | 0 | 0
raP_Dvc_D4SD | XRdy_St1 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_St1, enable button. | Read Only | 0 | 0
raP_Dvc_D4SD | XRdy_St2 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_St2, enable button. | Read Only | 0 | 0
raP_Dvc_D4SD | XRdy_St3 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_St3, enable button. | Read Only | 0 | 0
raP_Dvc_D4SD | XRdy_Reset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Reset, enable button. | Read Only | 0 | 0
raP_Dvc_D4SD | XRdy_ResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ResetAckAll, enable button. | Read Only | 0 | 0
raP_Dvc_D4SD | Val_Owner | Output | DINT |  | 0 | Decimal | 0 | 0 | Current object Owner ID, 0 = not owned. | Read Only | 0 | 0
raP_Dvc_nPos | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable output: The EnableOut signal is not manipulated by this instruction. Its output state always reflects EnableIn input state. | Read Only | 0
raP_Dvc_nPos | Out_Pos01Data | Output | BOOL | Wrk_bOut.1 | 0 | Decimal | 0 | 1 | Output to go to Position 1. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos02Data | Output | BOOL | Wrk_bOut.2 | 0 | Decimal | 0 | 1 | Output to go to Position 2. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos03Data | Output | BOOL | Wrk_bOut.3 | 0 | Decimal | 0 | 1 | Output to go to Position 3. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos04Data | Output | BOOL | Wrk_bOut.4 | 0 | Decimal | 0 | 1 | Output to go to Position 4. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos05Data | Output | BOOL | Wrk_bOut.5 | 0 | Decimal | 0 | 1 | Output to go to Position 5. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos06Data | Output | BOOL | Wrk_bOut.6 | 0 | Decimal | 0 | 1 | Output to go to Position 6. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos07Data | Output | BOOL | Wrk_bOut.7 | 0 | Decimal | 0 | 1 | Output to go to Position 7. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos08Data | Output | BOOL | Wrk_bOut.8 | 0 | Decimal | 0 | 1 | Output to go to Position 8 . | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos09Data | Output | BOOL | Wrk_bOut.9 | 0 | Decimal | 0 | 0 | Output to go to Position 9. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos10Data | Output | BOOL | Wrk_bOut.10 | 0 | Decimal | 0 | 0 | Output to go to Position 10. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos11Data | Output | BOOL | Wrk_bOut.11 | 0 | Decimal | 0 | 0 | Output to go to Position 11. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos12Data | Output | BOOL | Wrk_bOut.12 | 0 | Decimal | 0 | 0 | Output to go to Position 12. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos13Data | Output | BOOL | Wrk_bOut.13 | 0 | Decimal | 0 | 0 | Output to go to Position 13. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos14Data | Output | BOOL | Wrk_bOut.14 | 0 | Decimal | 0 | 0 | Output to go to Position 14. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos15Data | Output | BOOL | Wrk_bOut.15 | 0 | Decimal | 0 | 0 | Output to go to Position 15. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos16Data | Output | BOOL | Wrk_bOut.16 | 0 | Decimal | 0 | 0 | Output to go to Position 16. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos17Data | Output | BOOL | Wrk_bOut.17 | 0 | Decimal | 0 | 0 | Output to go to Position 17. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos18Data | Output | BOOL | Wrk_bOut.18 | 0 | Decimal | 0 | 0 | Output to go to Position 18 . | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos19Data | Output | BOOL | Wrk_bOut.19 | 0 | Decimal | 0 | 0 | Output to go to Position 19. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos20Data | Output | BOOL | Wrk_bOut.20 | 0 | Decimal | 0 | 0 | Output to go to Position 20. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos21Data | Output | BOOL | Wrk_bOut.21 | 0 | Decimal | 0 | 0 | Output to go to Position 21. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos22Data | Output | BOOL | Wrk_bOut.22 | 0 | Decimal | 0 | 0 | Output to go to Position 22. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos23Data | Output | BOOL | Wrk_bOut.23 | 0 | Decimal | 0 | 0 | Output to go to Position 23. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos24Data | Output | BOOL | Wrk_bOut.24 | 0 | Decimal | 0 | 0 | Output to go to Position 24. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos25Data | Output | BOOL | Wrk_bOut.25 | 0 | Decimal | 0 | 0 | Output to go to Position 25. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos26Data | Output | BOOL | Wrk_bOut.26 | 0 | Decimal | 0 | 0 | Output to go to Position 26. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos27Data | Output | BOOL | Wrk_bOut.27 | 0 | Decimal | 0 | 0 | Output to go to Position 27. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos28Data | Output | BOOL | Wrk_bOut.28 | 0 | Decimal | 0 | 0 | Output to go to Position 28 . | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos29Data | Output | BOOL | Wrk_bOut.29 | 0 | Decimal | 0 | 0 | Output to go to Position 29. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Pos30Data | Output | BOOL | Wrk_bOut.30 | 0 | Decimal | 0 | 0 | Output to go to Position 30. | Read Only | 0 | 0
raP_Dvc_nPos | Out_IncData | Output | BOOL |  | 0 | Decimal | 0 | 1 | Output to drive to Increasing Position ("clockwise"). | Read Only | 0 | 0
raP_Dvc_nPos | Out_DecData | Output | BOOL |  | 0 | Decimal | 0 | 1 | Output to drive to Decreasing Position ("counter-clockwise"). | Read Only | 0 | 0
raP_Dvc_nPos | Out_UnlockData | Output | BOOL |  | 0 | Decimal | 0 | 0 | Output to unlock / unseal device. | Read Only | 0 | 0
raP_Dvc_nPos | Out_LockData | Output | BOOL |  | 0 | Decimal | 0 | 0 | Output to lock / seal device. | Read Only | 0 | 0
raP_Dvc_nPos | Out_CylExtendData | Output | BOOL |  | 0 | Decimal | 0 | 0 | Output to Extend Cylinder to engage ratchet device. | Read Only | 0 | 0
raP_Dvc_nPos | Out_CylRetractData | Output | BOOL |  | 0 | Decimal | 0 | 0 | Output to Retract Cylinder to disengage ratchet device. | Read Only | 0 | 0
raP_Dvc_nPos | Out_CylLeftData | Output | BOOL |  | 0 | Decimal | 0 | 0 | Output to ratchet device to Left (increase position). | Read Only | 0 | 0
raP_Dvc_nPos | Out_CylRightData | Output | BOOL |  | 0 | Decimal | 0 | 0 | Output to ratchet device to Right (decrease position). | Read Only | 0 | 0
raP_Dvc_nPos | Out_HornData | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Sound audible prior to commanded energize/ state change. | Read Only | 0 | 0
raP_Dvc_nPos | Out_Reset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset command has been received and accepted. | Read Only | 0 | 0
raP_Dvc_nPos | Out_OwnerSts | Output | DINT |  | 0 | Decimal | 0 | 0 | Status of command source, owner command handshake and ready status. 0 = None, .10 = Operator Lock, .11 = Operator Unlock, .12 = Program Lock, .13 = Program Unlock, .14 = Acquire Maintenance, .15 = Release Maintenance, .16 = Acquire External, .17 = Release External, .18 = Has Maintenance, .19 = External Override Lock, .20 = Has External, .21 = Has Operator, .22 = Has Operator Locked, .23 = Has Program, .24 = Has Program Locked, .29 = Echo, .30 = Not Ready. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Initialized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Instruction is initialized. Use Inp_InitializeReq to reinitialize. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos01 | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device confirmed in Position 1. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos02 | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device confirmed in Position 2. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos03 | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device confirmed in Position 3. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos04 | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device confirmed in Position 4. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos05 | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device confirmed in Position 5. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos06 | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device confirmed in Position 6. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos07 | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device confirmed in Position 7. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos08 | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device confirmed in Position 8. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos09 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 9. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos10 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 10. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos11 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 11. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos12 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 12. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos13 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 13. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos14 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 14. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos15 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 15. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos16 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 16. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos17 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 17. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos18 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 18. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos19 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 19. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos20 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 20. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos21 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 21. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos22 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 22. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos23 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 23. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos24 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 24. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos25 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 25. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos26 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 26. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos27 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 27. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos28 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 28. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos29 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 29. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Pos30 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device confirmed in Position 30. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Moving | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device moving to target position, not yet achieved. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Horn | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Sounding audible prior to commanded energize/ state change. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Virtual | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = The instruction treats the device as virtual. The instruction acts as normal but the outputs are kept de-energized; 0 = The instruction operates the device normally. | Read Only | 0 | 0
raP_Dvc_nPos | SrcQ_IO | Output | SINT |  | 0 | Decimal | 0 | 0 | Source and quality of primary input or output. GOOD 0 = I/O live and confirmed good quality 1 = I/O live and assumed good quality 2 = No feedback configured, assumed good quality TEST 8 = Device simulated 9 = Device loopback simulation 10 = Manually entered value UNCERTAIN 16 = Live input, off-specification 17 = Value substituted at device/bus 18 = Value substituted by maintenance (Has and not Use) 19 = Shed, using last good value 20 = Shed, using replacement value BAD 32 = Signal failure (out-of-range, NaN, invalid combination) 33 = I/O channel fault 34 = I/O module fault 35 = Bad I/O configuration (for example, scaling parameters) | Read Only | 0 | 0
raP_Dvc_nPos | SrcQ | Output | SINT |  | 0 | Decimal | 0 | 0 | Final position source and quality. GOOD 0 = I/O live and confirmed good quality 1 = I/O live and assumed good quality 2 = No feedback configured, assumed good quality TEST 8 = Device simulated 9 = Device loopback simulation 10 = Manually entered value UNCERTAIN 16 = Live input, off-specification 17 = Value substituted at device/bus 18 = Value substituted by maintenance (Has and not Use) 19 = Shed, using last good value 20 = Shed, using replacement value BAD 32 = Signal failure (out-of-range, NaN, invalid combination) 33 = I/O channel fault 34 = I/O module fault 35 = Bad I/O configuration (for example, scaling parameters) | Read Only | 0 | 0
raP_Dvc_nPos | Sts_eCmd | Output | SINT |  | 0 | Decimal | 0 | 0 | Device command: 0 = None, 1 = Pos 1, 2 = Pos 2, ..., 30 = Pos 30. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_eFdbk | Output | SINT |  | 0 | Decimal | 0 | 0 | Device feedback: 0 = Moving, 1 = Pos 1, 2 = Pos 2,.., 30 = Pos 30, 31 = Multiple positions (invalid). | Read Only | 0 | 0
raP_Dvc_nPos | Sts_eSts | Output | SINT |  | 0 | Decimal | 0 | 0 | Device Confirmed Satus 0 = Powerup/Reset, 1 = Position 1, 2 = Position 2, ..., 30 = Position 30, 31 = Moving, 32 = Horn sounding. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_eFault | Output | SINT |  | 0 | Decimal | 0 | 0 | Device Fault Status 0 = None, 16 = Position Fault, 17 = Lock Fault, 32 = I/O Fault, 34 = Configuration error. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_eState | Output | SINT |  | 0 | Decimal | 0 | 0 | Internal State: 0 = reset/unknown, 1 = in position, 2 = unlocking, 3 = moving to position 1, 4 = moving to requested position, 5 = locking, 6 = faulted. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_eOutPos | Output | SINT |  | 0 | Decimal | 0 | 0 | State of position outputs to physical device: 0 = De-energized, 1 = Position 1, 2 = Position 2, ..., 30 = Position 30. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_eOutState | Output | SINT |  | 0 | Decimal | 0 | 0 | State of motion outputs to physical device: 0 = Maintain position, 1 = Unlock, 2 = Decrease position, 3 = Increase position, 4 = Lock, 5 = Horn. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_eNotify | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_eNotifyAll | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values including related objects: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_eNotifyIOFault | Output | SINT |  | 0 | Decimal | 0 | 0 | I/OFault alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_eNotifyPosFail | Output | SINT |  | 0 | Decimal | 0 | 0 | Device position fail alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_eNotifyLockFail | Output | SINT |  | 0 | Decimal | 0 | 0 | Device lock / seal fail alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_eNotifyIntlkTrip | Output | SINT |  | 0 | Decimal | 0 | 0 | Interlock Trip alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_UnackAlmCount | Output | SINT |  | 0 | Decimal | 0 | 0 | Count of Unacknowledged Alarms. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_eSrc | Output | INT | CmdSrc.Sts_eSrc | 0 | Decimal | 0 | 0 | The current command source enumerated values: 0 = Logic not in use, 4 = Hand, 8 = Maintenance, 16 = Override, 32 = Program, 33 = Program locked, 34 = Program by default (Normal), 64 = Operator, 65 = Operator locked, 66 = Operator by default (Normal), 128 = Maintenance Out of service, 129 = Programmed Out of service (rung false), 256 = External. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_bSrc | Output | INT | CmdSrc.Sts_bSrc | 0 | Decimal | 0 | 0 | Active selection bitmap (for HMI totem pole with command source request selection): Sts_bSrc.0: hand, Sts_bSrc.1: Programmed Out of service (rung false), Sts_bSrc.2: Maintenance Out of service, Sts_bSrc.3: Maintenance, Sts_bSrc.4: Override, Sts_bSrc.5: External, Sts_bSrc.6: Program locked, Sts_bSrc.7: Program, Sts_bSrc.8: Operator locked, Sts_bSrc.9: Operator. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Available | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device has been acquired by Program and is now available for control. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_IntlkAvailable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device can be acquired by Program and is available for control when interlocks are OK. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Bypass | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Bypassable interlocks and permissives are bypassed. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_BypActive | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = A maintenance bypass is active, display breadcrumb. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_MaintByp | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device has a maintenance bypass function active. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_NotRdy | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready, see detail bits (Sts_Nrdyxxx) for reason. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_NrdyCfgErr | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready: configuration error. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_NrdyPosFail | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready: device position failure, shed requires reset. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_NrdyLockFail | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready: device lock / seal failure, shed requires reset. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_NrdyIntlk | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready: Interlock not OK. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_NrdyIOFault | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready: I/O Fault, shed requires reset. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_NrdyOoS | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready: device is Out of Service. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_NrdyPerm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready: permissive not OK. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_NrdyPrioPos1 | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready: operator or external priority Position 1 command, shed requires reset. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Error in Configuration, see detail bits (Sts_ErrXxx) for reason. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_ErrAlm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in Logix tag-based alarm settings. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_ErrExtendDelay | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Invalid delay before cylinder extend/retract. Use 0.0 to 2147483.0 seconds. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_ErrVerifyDelay | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Invalid delay before position verify. Use 0.0 to 2147483.0 seconds. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_ErrPosCheckTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Invalid position check time. Use 0.0 to 2147483.0 seconds. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_ErrLockCheckTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Invalid lock check time. Use 0.0 to 2147483.0 seconds. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_ErrVirtualPosTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Invalid virtual position feedback time. Use 0.0 to 2147483.0 seconds. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_ErrVirtualLockTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Invalid virtual lock feedback time. Use 0.0 to 2147483.0 seconds. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_ErrVirtualCylTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Invalid virtual cylinder feedback time. Use 0.0 to 2147483.0 seconds. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Hand | Output | BOOL | CmdSrc.Sts_Hand | 0 | Decimal | 0 | 1 | 1 = Hand is selected (supersedes OoS, Maintenance, Override, External, Program, Operator). | Read Only | 0 | 0
raP_Dvc_nPos | Sts_OoS | Output | BOOL | CmdSrc.Sts_OoS | 0 | Decimal | 0 | 1 | 1 = Out of service is selected (supersedes Maintenance, Override, External, Program, Operator). | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Maint | Output | BOOL | CmdSrc.Sts_Maint | 0 | Decimal | 0 | 1 | 1 = Maintenance is selected (supersedes Override, External, Program, Operator). | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Ovrd | Output | BOOL | CmdSrc.Sts_Ovrd | 0 | Decimal | 0 | 1 | 1 = Override is selected (supersedes External, Program, Operator). | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Ext | Output | BOOL | CmdSrc.Sts_Ext | 0 | Decimal | 0 | 1 | 1 = External is selected (supersedes Program and Operator). | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Prog | Output | BOOL | CmdSrc.Sts_Prog | 0 | Decimal | 0 | 1 | 1 = Program is selected. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_ProgLocked | Output | BOOL | CmdSrc.Sts_ProgLocked | 0 | Decimal | 0 | 0 | 1 = Program is selected and Locked. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Oper | Output | BOOL | CmdSrc.Sts_Oper | 0 | Decimal | 0 | 1 | 1 = Operator is selected. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_OperLocked | Output | BOOL | CmdSrc.Sts_OperLocked | 0 | Decimal | 0 | 0 | 1 = Operator is selected and Locked. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_ProgOperSel | Output | BOOL | CmdSrc.Sts_ProgOperSel | 0 | Decimal | 0 | 0 | Program/Operator selection (latch) state: 1 = Program, 0 = Operator. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_ProgOperLock | Output | BOOL | CmdSrc.Sts_ProgOperLock | 0 | Decimal | 0 | 1 | Program/Operator lock (latch) state, 1 = Locked, 0 = Unlocked. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Normal | Output | BOOL | CmdSrc.Sts_Normal | 0 | Decimal | 0 | 0 | 1 = Selection equals the Normal (Program or Operator). | Read Only | 0 | 0
raP_Dvc_nPos | Sts_ExtReqInh | Output | BOOL | CmdSrc.Sts_ExtReqInh | 0 | Decimal | 0 | 0 | 1 = External request inhibited, cannot get to External from current state. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_ProgReqInh | Output | BOOL | CmdSrc.Sts_ProgReqInh | 0 | Decimal | 0 | 0 | 1 = Program request inhibited, cannot get to Program from current state. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_MAcqRcvd | Output | BOOL | CmdSrc.Sts_MAcqRcvd | 0 | Decimal | 0 | 0 | 1 = Maintenance acquire command received this scan. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_Alm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is active. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_AlmInh | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is shelved or disabled. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_IOFault | Output | BOOL |  | 0 | Decimal | 0 | 0 | I/O Fault status: 1 = Bad, 0 = OK. There is a predefined default discrete Logix tag-based alarm for the status. Set standard configuration members of the discrete Logix tag-based alarm. Alarm elements can be accessed as follows: nPosTag.@Alarms.Alm_IOFault.AlarmElement. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_PosFail | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device position failure. There is a predefined default discrete Logix tag-based alarm for the status. Set standard configuration members of the discrete Logix tag-based alarm. Alarm elements can be accessed as follows: nPosTag.@Alarms.Alm_PosFail.AlarmElement. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_LockFail | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device lock/seal failure. There is a predefined default discrete Logix tag-based alarm for the status. Set standard configuration members of the discrete Logix tag-based alarm. Alarm elements can be accessed as follows: nPosTag.@Alarms.Alm_LockFail.AlarmElement. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_IntlkTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device de-energized or set to Position 1 by an interlock Not OK. There is a predefined default discrete Logix tag-based alarm for the status. Set standard configuration members of the discrete Logix tag-based alarm. Alarm elements can be accessed as follows: nPosTag.@Alarms.Alm_IntlkTrip.AlarmElement. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_RdyAck | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is ready to be acknowledged. | Read Only | 0 | 0
raP_Dvc_nPos | Sts_RdyReset | Output | BOOL | ORdy_Reset | 0 | Decimal | 0 | 0 | 1 = A latched alarm or shed condition is ready to be reset. | Read Only | 0 | 0
raP_Dvc_nPos | XRdy_Acq | Output | BOOL | CmdSrc.XRdy_Acq | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Acq, enable button. | Read Only | 0 | 0
raP_Dvc_nPos | XRdy_Rel | Output | BOOL | CmdSrc.XRdy_Rel | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Rel, enable button. | Read Only | 0 | 0
raP_Dvc_nPos | XRdy_Pos | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XSet_Pos, enable entry. | Read Only | 0 | 0
raP_Dvc_nPos | XRdy_Reset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Reset, enable button. | Read Only | 0 | 0
raP_Dvc_nPos | XRdy_ResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ResetAckAll, enable button. | Read Only | 0 | 0
raP_Dvc_nPos | Val_Owner | Output | DINT |  | 0 | Decimal | 0 | 0 | Current Object Owner ID (0 = not owned). | Read Only | 0 | 0
raP_Dvc_VlvMP | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable output: The EnableOut signal is not manipulated by this instruction. Its output state always reflects EnableIn input state. | Read Only | 0
raP_Dvc_VlvMP | Out_OpenData | Output | BOOL |  | 0 | Decimal | 0 | 1 | Output to Open valve, 1 = Open. | Read Only | 0 | 0
raP_Dvc_VlvMP | Out_CloseData | Output | BOOL |  | 0 | Decimal | 0 | 1 | Output to Close valve, 1 = Close. | Read Only | 0 | 0
raP_Dvc_VlvMP | Out_LiftLowerData | Output | BOOL |  | 0 | Decimal | 0 | 1 | Output to Lift lower valve seat, 1 = Lift. | Read Only | 0 | 0
raP_Dvc_VlvMP | Out_LiftUpperData | Output | BOOL |  | 0 | Decimal | 0 | 1 | Output to Lift upper valve seat, 1 = Lift. | Read Only | 0 | 0
raP_Dvc_VlvMP | Out_CavityInletData | Output | BOOL |  | 0 | Decimal | 0 | 0 | Output to Open leakage cavity cleaning inlet, 1 = Open. | Read Only | 0 | 0
raP_Dvc_VlvMP | Out_CavityOutletData | Output | BOOL |  | 0 | Decimal | 0 | 0 | Output to Close leakage cavity drain / cleaning outlet, 1 = Close. | Read Only | 0 | 0
raP_Dvc_VlvMP | Out_HornData | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Sound audible prior to commanded valve action. | Read Only | 0 | 0
raP_Dvc_VlvMP | Out_Reset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset command has been received and accepted. | Read Only | 0 | 0
raP_Dvc_VlvMP | Out_OwnerSts | Output | DINT |  | 0 | Decimal | 0 | 0 | Status of command source, owner command handshake and ready status. 0 = None, .10 = Operator Lock, .11 = Operator Unlock, .12 = Program Lock, .13 = Program Unlock, .14 = Acquire Maintenance, .15 = Release Maintenance, .16 = Acquire External, .17 = Release External, .18 = Has Maintenance, .19 = External Override Lock, .20 = Has External, .21 = Has Operator, .22 = Has Operator Locked, .23 = Has Program, .24 = Has Program Locked, .29 = Echo, .30 = Not Ready. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Initialized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Instruction is initialized. Use Inp_InitializeReq to reinitialize. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Closed | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Valve closed position achieved. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Opened | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Valve open position achieved. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_LiftLower | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Lift valve lower seat position achieved. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_LiftUpper | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Lift valve upper seat position achieved. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_CleanCavity | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Clean valve leakage cavity position achieved. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_CleanLower | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Clean valve lower seat position achieved. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_CleanUpper | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Clean valve upper seat position achieved. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Moving | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Valve moving to target position, not yet achieved. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Pulsing | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Pulsing valve seat for cleaning. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Horn | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Valve audible alert (Horn) is active. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Physical | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = The instruction is available to control the physical valve, 0 = Instruction is not controlling the physical valve, outputs are holding the valve closed. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Virtual | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = The instruction treats the valve as virtual. The instruction acts as normal but the outputs are kept de-energized; 0 = The instruction operates the valve normally. | Read Only | 0 | 0
raP_Dvc_VlvMP | SrcQ_IO | Output | SINT |  | 0 | Decimal | 0 | 0 | Source and quality of primary input or output. GOOD 0 = I/O live and confirmed good quality 1 = I/O live and assumed good quality 2 = No feedback configured, assumed good quality TEST 8 = Device simulated 9 = Device loopback simulation 10 = Manually entered value UNCERTAIN 16 = Live input, off-specification 17 = Value substituted at device/bus 18 = Value substituted by maintenance (Has and not Use) 19 = Shed, using last good value 20 = Shed, using replacement value BAD 32 = Signal failure (out-of-range, NaN, invalid combination) 33 = I/O channel fault 34 = I/O module fault 35 = Bad I/O configuration (for example, scaling parameters) | Read Only | 0 | 0
raP_Dvc_VlvMP | SrcQ | Output | SINT |  | 0 | Decimal | 0 | 0 | Source and quality of primary value or status. GOOD 0 = I/O live and confirmed good quality 1 = I/O live and assumed good quality 2 = No feedback configured, assumed good quality TEST 8 = Device simulated 9 = Device loopback simulation 10 = Manually entered value UNCERTAIN 16 = Live input, off-specification 17 = Value substituted at device/bus 18 = Value substituted by maintenance (Has and not Use) 19 = Shed, using last good value 20 = Shed, using replacement value BAD 32 = Signal failure (out-of-range, NaN, invalid combination) 33 = I/O channel fault 34 = I/O module fault 35 = Bad I/O configuration (for example, scaling parameters) | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_eCmd | Output | SINT |  | 0 | Decimal | 0 | 0 | Valve Command: 0 = None, 1 = Close, 3 = Open, 4 = Lift lower seat, 5 = Lift upper seat, 6 = Clean cavity, 8 = Clean lower seat, 10 = Clean upper seat. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_eSts | Output | SINT |  | 0 | Decimal | 0 | 0 | Valve confirmed status: 0 = Unknown, 1 = Closed, 3 = Opened, 4 = Lift lower seat, 5 = Lift upper seat, 6 = Clean cavity, 8 = Clean lower seat, 10 = Clean upper seat, 11 = Moving, 12 = Pulse lower seat, 13 = Pulse upper seat, 14 = Horn. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_eState | Output | SINT |  | 0 | Decimal | 0 | 0 | Valve state number for HMI state diagram (see instruction help) (enumeration). | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_eFault | Output | SINT |  | 0 | Decimal | 0 | 0 | Valve fault status: 0 = None, 16 = Position fail, 32 = I/O fault, 34 = Configuration error. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_eNotify | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_eNotifyAll | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values including related objects: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_eNotifyIOFault | Output | SINT |  | 0 | Decimal | 0 | 0 | I/OFault alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_eNotifyFail | Output | SINT |  | 0 | Decimal | 0 | 0 | Position fail alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_eNotifyIntlkTrip | Output | SINT |  | 0 | Decimal | 0 | 0 | Interlock Trip alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_UnackAlmCount | Output | SINT |  | 0 | Decimal | 0 | 0 | Count of unacknowledged alarms. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_eSrc | Output | INT | CmdSrc.Sts_eSrc | 0 | Decimal | 0 | 0 | The current command source enumerated values: 0 = Logic not in use, 4 = Hand, 8 = Maintenance, 16 = Override, 32 = Program, 33 = Program locked, 34 = Program by default (Normal), 64 = Operator, 65 = Operator locked, 66 = Operator by default (Normal), 128 = Maintenance Out of service, 129 = Programmed Out of service (rung false), 256 = External. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_bSrc | Output | INT | CmdSrc.Sts_bSrc | 0 | Decimal | 0 | 0 | Active selection bitmap (for HMI totem pole with command source request selection): Sts_bSrc.0: hand, Sts_bSrc.1: Programmed Out of service (rung false), Sts_bSrc.2: Maintenance Out of service, Sts_bSrc.3: Maintenance, Sts_bSrc.4: Override, Sts_bSrc.5: External, Sts_bSrc.6: Program locked, Sts_bSrc.7: Program, Sts_bSrc.8: Operator locked, Sts_bSrc.9: Operator. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Available | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Valve has been acquired by Program and is now available for control. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_IntlkAvailable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Valve can be acquired by Program and is available for control when interlocks are OK. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Bypass | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Bypassable interlocks and permissives are bypassed. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_BypActive | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Interlock / permissive bypassing active (bypassed or maintenance). | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_MaintByp | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device has a maintenance bypass function active. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_NotRdy | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready, see detail bits (Sts_Nrdyxxx) for reason. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_NrdyCfgErr | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready: Configuration error. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_NrdyFail | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready: Position failure (Shed Requires Reset). | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_NrdyIntlk | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready: Interlock not OK. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_NrdyIOFault | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready: I/O Fault (Shed requires Reset). | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_NrdyOoS | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready: Device out of service. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_NrdyPerm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready: Permissive Not OK. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_NrdyPrioClose | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready: Operator or External priority Close command requires reset. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_NrdyVirtualPhysical | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready: Valve is transitioning between physical and virtual operation. | Read/Write | 0 | 0
raP_Dvc_VlvMP | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Error in configuration: See detail bits (Sts_Errxxx) for reason. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_ErrAlm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in Logix tag-based alarm settings. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_bErrFdbkTime | Output | INT |  | 2#0000_0000_0000_0000 | Binary | 0 | 0 | Bitmapped, a set bit indicates an error in that state's feedback confirmation time. Use 0.0 to 60.0 seconds. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_ErrOpenPulseTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in Config: Invalid open pulse time: use 0.0 to 2147483.0 seconds. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_ErrClosePulseTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in Config: Invalid close pulse time: use 0.0 to 2147483.0 seconds. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_ErrFailTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in Config: Invalid position fail time: use 0.0 to 2147483.0 seconds. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Hand | Output | BOOL | CmdSrc.Sts_Hand | 0 | Decimal | 0 | 1 | 1 = Hand is selected (supersedes OoS, Maintenance, Override, External, Program, Operator). | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_OoS | Output | BOOL | CmdSrc.Sts_OoS | 0 | Decimal | 0 | 1 | 1 = Out of service is selected (supersedes Maintenance, Override, External, Program, Operator). | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Maint | Output | BOOL | CmdSrc.Sts_Maint | 0 | Decimal | 0 | 1 | 1 = Maintenance is selected (supersedes Override, External, Program, Operator). | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Ovrd | Output | BOOL | CmdSrc.Sts_Ovrd | 0 | Decimal | 0 | 1 | 1 = Override is selected (supersedes External, Program, Operator). | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Ext | Output | BOOL | CmdSrc.Sts_Ext | 0 | Decimal | 0 | 1 | 1 = External is selected (supersedes Program and Operator). | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Prog | Output | BOOL | CmdSrc.Sts_Prog | 0 | Decimal | 0 | 1 | 1 = Program is selected. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_ProgLocked | Output | BOOL | CmdSrc.Sts_ProgLocked | 0 | Decimal | 0 | 0 | 1 = Program is selected and Locked. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Oper | Output | BOOL | CmdSrc.Sts_Oper | 0 | Decimal | 0 | 1 | 1 = Operator is selected. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_OperLocked | Output | BOOL | CmdSrc.Sts_OperLocked | 0 | Decimal | 0 | 0 | 1 = Operator is selected and Locked. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_ProgOperSel | Output | BOOL | CmdSrc.Sts_ProgOperSel | 0 | Decimal | 0 | 0 | Program/Operator selection (latch) state: 1 = Program, 0 = Operator. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_ProgOperLock | Output | BOOL | CmdSrc.Sts_ProgOperLock | 0 | Decimal | 0 | 1 | Program/Operator lock (latch) state, 1 = Locked, 0 = Unlocked. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Normal | Output | BOOL | CmdSrc.Sts_Normal | 0 | Decimal | 0 | 0 | 1 = Selection equals the Normal (Program or Operator). | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_ExtReqInh | Output | BOOL | CmdSrc.Sts_ExtReqInh | 0 | Decimal | 0 | 0 | 1 = External request inhibited, cannot get to External from current state. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_ProgReqInh | Output | BOOL | CmdSrc.Sts_ProgReqInh | 0 | Decimal | 0 | 0 | 1 = Program request inhibited, cannot get to Program from current state. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_MAcqRcvd | Output | BOOL | CmdSrc.Sts_MAcqRcvd | 0 | Decimal | 0 | 0 | 1 = Maintenance acquire command received this scan. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_CmdConflict | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Conflicting commands received this scan. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Alm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is active. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_AlmInh | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is shelved or disabled. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_IOFault | Output | BOOL |  | 0 | Decimal | 0 | 0 | I/O Fault status: 1 = Bad, 0 = OK. There is a predefined default discrete Logix tag-based alarm for the status. Set standard configuration members of the discrete Logix tag-based alarm. Alarm elements can be accessed as follows: ValveMPTag.@Alarms.Alm_IOFault.AlarmElement. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_Fail | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Valve position failure. There is a predefined default discrete Logix tag-based alarm for the status. Set standard configuration members of the discrete Logix tag-based alarm. Alarm elements can be accessed as follows: ValveMPTag.@Alarms.Alm_Fail.AlarmElement. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_IntlkTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Valve closed by an interlock Not OK. There is a predefined default discrete Logix tag-based alarm for the status. Set standard configuration members of the discrete Logix tag-based alarm. Alarm elements can be accessed as follows: ValveMPTag.@Alarms.Alm_IntlkTrip.AlarmElement. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_RdyAck | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is ready to be acknowledged. | Read Only | 0 | 0
raP_Dvc_VlvMP | Sts_RdyReset | Output | BOOL | ORdy_Reset | 0 | Decimal | 0 | 0 | 1 = A latched alarm or shed condition is ready to be reset. | Read Only | 0 | 0
raP_Dvc_VlvMP | XRdy_Acq | Output | BOOL | CmdSrc.XRdy_Acq | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Acq, enable HMI button. | Read Only | 0 | 0
raP_Dvc_VlvMP | XRdy_Rel | Output | BOOL | CmdSrc.XRdy_Rel | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Rel, enable HMI button. | Read Only | 0 | 0
raP_Dvc_VlvMP | XRdy_Close | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Close, enable button. | Read Only | 0 | 0
raP_Dvc_VlvMP | XRdy_Open | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Open, enable button. | Read Only | 0 | 0
raP_Dvc_VlvMP | XRdy_LiftLower | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_LiftLower, enable button. | Read Only | 0 | 0
raP_Dvc_VlvMP | XRdy_LiftUpper | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_LiftUpper, enable button. | Read Only | 0 | 0
raP_Dvc_VlvMP | XRdy_CleanCavity | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_CleanCavity, enable button. | Read Only | 0 | 0
raP_Dvc_VlvMP | XRdy_CleanLower | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_CleanLower, enable button. | Read Only | 0 | 0
raP_Dvc_VlvMP | XRdy_CleanUpper | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_CleanUpper, enable button. | Read Only | 0 | 0
raP_Dvc_VlvMP | XRdy_Reset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Reset, enable button. | Read Only | 0 | 0
raP_Dvc_VlvMP | XRdy_ResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ResetAckAll, enable button. | Read Only | 0 | 0
raP_Dvc_VlvMP | Val_Owner | Output | DINT |  | 0 | Decimal | 0 | 0 | Current Object Owner ID (0=not owned). | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Out_Reset | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Reset command has been received and accepted. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Val_Check | Output | DINT |  | 16#0000_0000 | Hex | 0 | 1 | Current application check-for-change value. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Val_Year | Output | DINT |  | 0 | Decimal | 0 | 1 | Current year on controller clock (local time and date). | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Val_Month | Output | DINT |  | 0 | Decimal | 0 | 1 | Current month on controller clock (local time and date). | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Val_Day | Output | DINT |  | 0 | Decimal | 0 | 1 | Current day on controller clock (local time and date). | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Val_Hour | Output | DINT |  | 0 | Decimal | 0 | 1 | Current hour on controller clock (local time and date). | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Val_Minute | Output | DINT |  | 0 | Decimal | 0 | 1 | Current minute on controller clock (local time and date). | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Val_Second | Output | DINT |  | 0 | Decimal | 0 | 1 | Current second on controller clock (local time and date). | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Val_Microsecond | Output | DINT |  | 0 | Decimal | 0 | 0 | Current microsecond on controller clock (local time and date). | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Val_DayOfWeek | Output | DINT |  | 0 | Decimal | 0 | 1 | Current day of the week based on controller date, 0 = Sunday, 1 = Monday, ..., 6 = Saturday. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_Initialized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Instruction is initialized. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_OnlineChange | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Change detected: an online change or partial import. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_NoChangeDownload | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Change detected: the same application was downloaded, but configuration data may have changed. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_ChangeDownload | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Change detected: a changed application was downloaded. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_EditsDownload | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Change detected: an application with offline edits was downloaded. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_RestoreFromFlash | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Change detected: the application was restored from memory card (CF/SD). | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_FaultMode | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Controller Mode is FAULTED. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_RunMode | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Controller Mode is RUN. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_ProgMode | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Controller Mode is PROGRAM. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_MinorRecovFlt | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Controller has a Minor Recoverable Fault. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_MinorUnrecovFlt | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Controller has a Minor Unrecoverable Fault. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_MajorRecovFlt | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Controller has a Major Recoverable Fault. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_MajorUnrecovFlt | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Controller has a Major Unrecoverable Fault. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_KeyswRun | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Controller Keyswitch is in the RUN position. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_KeyswRem | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Controller Keyswitch is in the REMOTE position. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_KeyswProg | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Controller Keyswitch is in the PROGRAM position. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_Timing | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Waiting for update time to finish before reading controller status. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_Busy | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Instruction is communicating with controller to get its status. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_Done | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Data collection is complete, status and values have been updated. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_MsgErr | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Message error occurred, unable to read at least one iterm. Check the MSG Path. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_ChangeDetected | Output | BOOL |  | 0 | Decimal | 0 | 0 | Change detected alarm: 1 = Change in controller logic detected, raise alarm; 0 = no alarm: no controller logic changes since last reset. There is a predefined default discrete Logix tag-based alarm for the status. Set standard configuration members of the discrete Logix tag-based alarm. Alarm elements can be accessed as follows: D4SDTag.@Alarms.Alm_IOFault.AlarmElement. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_eNotify | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_eNotifyAll | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values including related objects: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_eNotifyChangeDetected | Output | SINT |  | 0 | Decimal | 0 | 0 | Change detected alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_UnackAlmCount | Output | DINT |  | 0 | Decimal | 0 | 0 | Count of Unacknowledged Alarms. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Error in Configuration, see detail bits (Sts_ErrXxx) for reason. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_ErrAlm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in Logix tag-based alarm settings. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_Alm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is active. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_AlmInh | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is shelved or disabled. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_RdyAck | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is ready to be acknowledged. | Read Only | 0 | 0
raP_Dvc_LgxChangeDet | Sts_RdyReset | Output | BOOL | ORdy_Reset | 0 | Decimal | 0 | 0 | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only | 0 | 0
raP_Dvc_LgxCPU_5x80 | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Dvc_LgxCPU_5x80 | Sts_Initialized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Instruction is initialized. | Read Only | 0 | 0
raP_Dvc_LgxCPU_5x80 | Sts_Enabled | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Maintenance has enabled CPU data collection. | Read Only | 0 | 0
raP_Dvc_LgxCPU_5x80 | Sts_Timing | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Instruction is waiting for update time to complete. | Read Only | 0 | 0
raP_Dvc_LgxCPU_5x80 | Sts_Busy | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Instruction is polling CPU data from controller. | Read Only | 0 | 0
raP_Dvc_LgxCPU_5x80 | Sts_Done | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Data collection complete, CPU data in Ref_Out tag have been updated. | Read Only | 0 | 0
raP_Dvc_LgxCPU_5x80 | Sts_MSGError | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Message error occurred, unable to read at least one CPU metric. | Read Only | 0 | 0
raP_Dvc_LgxCPU_5x80 | Sts_WrongVersion | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Wrong firmware version (must be 28.x or later) or controller is not supported | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Out_Reset | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Reset command has been received and accepted. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Out_Child_IO_OK | Output | BOOL |  | 1 | Decimal | 0 | 1 | 1 = This and all parent (grandparent, etc.) I/O OK, 0 = I/O Faulted. | Read/Write | 0 | 0
raP_Dvc_LgxModuleSts | Out_Child_IO_AlmGate | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Allow child Module Fault alarm, 0 = This instance (or parent) is raising Module Fault alarm, inhibit child alarm. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_Initialized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Instruction is initialized. Use Inp_InitializeReq to reinitialize. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_IOFault | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = This or parent I/O communication faulted (module not in Running state). Use this parameter to trigger device I/O Fault action. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_Connected | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = This module's connection is up and running. This paramter reports physical connection OK status regardless of bypass selection. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_Inhibited | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = This module's connection is inhibited, This paramter reports physical connection inhibit status regardless of bypass selection. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_AnyChanUncertain | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Any I/O channel on this module is uncertain, 0 = All channels OK. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_Virtual | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Using virtual connection status instead of the module's actual connection status. 0 = The instruction evaluates the module's connection status normally. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_Bypass | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Connection checking has been bypassed, state is always reported as Connected; 0 = The instruction checks the connection state normally. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_BypActive | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Interlock / permissive bypassing active (bypassed or maintenance). | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_eNotify | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_eNotifyAll | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values including related objects: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_eNotifyModuleFault | Output | SINT |  | 0 | Decimal | 0 | 0 | Module communication fault alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_eNotifyAnyChanFault | Output | SINT |  | 0 | Decimal | 0 | 0 | Any I/O channel fault alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_UnackAlmCount | Output | DINT |  | 0 | Decimal | 0 | 0 | Count of Unacknowledged Alarms. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Error in Configuration, see detail bits (Sts_ErrXxx) for reason. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_ErrAlm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in Logix tag-based alarm settings. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_ErrModuleFaultOnDly | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in Module communication fault on-delay configuration. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_Alm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is active. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_AlmInh | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is shelved or disabled. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_ModuleFault | Output | BOOL |  | 0 | Decimal | 0 | 1 | I/O Module communication fault alarm: 1 = Communication fault, raise alarm; 0 = no alarm: either communication is OK or parent device has raised an alarm. There is a predefined default discrete Logix tag-based alarm for the status. Set standard configuration members of the discrete Logix tag-based alarm. Alarm elements can be accessed as follows: D4SDTag.@Alarms.Alm_IOFault.AlarmElement. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_AnyChanFault | Output | BOOL |  | 0 | Decimal | 0 | 1 | Any I/O channel fault alarm: 1 = Channel fault, raise alarm; 0 = no alarm: no channel faults reported. There is a predefined default discrete Logix tag-based alarm for the status. Set standard configuration members of the discrete Logix tag-based alarm. Alarm elements can be accessed as follows: D4SDTag.@Alarms.Alm_IOFault.AlarmElement. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_RdyAck | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is ready to be acknowledged. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | Sts_RdyReset | Output | BOOL | ORdy_Reset | 0 | Decimal | 0 | 0 | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | XRdy_Reset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Reset, enable button. | Read Only | 0 | 0
raP_Dvc_LgxModuleSts | XRdy_ResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ResetAckAll, enable button. | Read Only | 0 | 0
raP_Dvc_LgxRedun | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Dvc_LgxRedun | Out_Reset | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Reset command has been received and accepted. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_eChasAState | Output | SINT |  | 0 | Decimal | 0 | 0 | Chassis A State: 1 = ????, 2 = PRIM, 3 = PWDS, 4 = PWNS, 8 = SYNC, 9 = DISQ. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_eChasBState | Output | SINT |  | 0 | Decimal | 0 | 0 | Chassis B State: 1 = ????, 2 = PRIM, 3 = PWDS, 4 = PWNS, 8 = SYNC, 9 = DISQ. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_eCtrlrAState | Output | SINT |  | 0 | Decimal | 0 | 0 | Controller A State: 1 = ????, 2 = PRIM, 3 = PWDS, 4 = PWNS, 6 = SNCG, 7 = SNCG, 8 = SYNC, 9 = DISQ, 14 = NONE. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_eCtrlrBState | Output | SINT |  | 0 | Decimal | 0 | 0 | Controller B State: 1 = ????, 2 = PRIM, 3 = PWDS, 4 = PWNS, 6 = SNCG, 7 = SNCG, 8 = SYNC, 9 = DISQ, 14 = NONE. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_eCtrlrAMode | Output | SINT |  | 0 | Decimal | 0 | 0 | Controller A Mode: 0 = PWRUP, 1 = PROG, 2 = RUN, 3 = TEST, 4 = FLTD, 5 = R->P, 6 = T->P, 7 = P->R, 8 = T->R, 9 = R->T, 10 = P->T, 11 = FLTG. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_eCtrlrBMode | Output | SINT |  | 0 | Decimal | 0 | 0 | Controller B Mode: 0 = PWRUP, 1 = PROG, 2 = RUN, 3 = TEST, 4 = FLTD, 5 = R->P, 6 = T->P, 7 = P->R, 8 = T->R, 9 = R->T, 10 = P->T, 11 = FLTG. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_eCtrlrAKeyswitch | Output | SINT |  | 0 | Decimal | 0 | 0 | Controller A Keyswitch Position: 0 = ????, 1 = RUN, 2 = PROG, 3 = REM. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_eCtrlrBKeyswitch | Output | SINT |  | 0 | Decimal | 0 | 0 | Controller B Keyswitch Position: 0 = ????, 1 = RUN, 2 = PROG, 3 = REM. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_bCtrlrAMinorFaults | Output | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | Controller A Minor Fault Bits: .4 = PROG, .6 = TASK, .9 = PORT, .10 = BATT. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_bCtrlrBMinorFaults | Output | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | Controller B Minor Fault Bits: .4 = PROG, .6 = TASK, .9 = PORT, .10 = BATT. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_eCompat | Output | INT |  | 0 | Decimal | 0 | 1 | A-vs-B-Module Compatibility: 0 = Unknown, 1 = Not compatible, 2 = Fully compatible, 3 = Standby compatible. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Val_QualProgress | Output | INT |  | 0 | Decimal | 0 | 1 | Backup Qualification Progress Percent Complete, 0 to 100, -1 = qualification not active. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Val_XferSizeLast | Output | DINT |  | 0 | Decimal | 0 | 1 | Number of 32-bit data words from Primary to Secondary in most recent data transfer. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Val_XferSizeMax | Output | DINT |  | 0 | Decimal | 0 | 1 | Number of 32-bit data words from Primary to Secondary: high water mark. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_Initialized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Instruction is initialized. Use Inp_InitializeReq to reinitialize. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_PriChassis | Output | BOOL |  | 0 | Decimal | 0 | 1 | 0 = Chassis A is currently Primary, 1 = Chassis B is currently Primary. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_SyncBusy | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Synchronize requested, sending command to RM/SRM. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_SyncDone | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Synchronize request to RM sent without error. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_SyncErr | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Synchronize request MSG to RM had an error: check Cfg_SlotXX for RM. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_SwitchoverBusy | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Switchover to secondary controller requested, sending command to RM. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_SwitchoverDone | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Switchover to secondary controller request to RM sent without error. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_SwitchoverErr | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Switchover to secondary controller MSG to RM had an error: check Cfg_SlotXX for Controller | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_eSts | Output | SINT |  | 0 | Decimal | 0 | 1 | Confirmed Status 0 = Unknown, 1 = Synchronized (Secondary is ready), 2 = Synchronizing, 3 = Secondary disqualified, 4 = Secondary not present. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_eFault | Output | SINT |  | 0 | Decimal | 0 | 1 | Fault Status 0 = None, 16 = Secondary Not Ready, 17 = No communication with RM, 34 = configuration error. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_eNotify | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_eNotifyAll | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values including related objects: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_eNotifySecNotRdy | Output | SINT |  | 0 | Decimal | 0 | 0 | Secondary controller not ready to take control status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_UnackAlmCount | Output | DINT |  | 0 | Decimal | 0 | 0 | Count of Unacknowledged Alarms. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Error in Configuration, see detail bits (Sts_ErrXxx) for reason. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_ErrAlm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in Logix tag-based alarm settings. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_Alm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is active. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_AlmInh | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is shelved or disabled. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_SecNotRdy | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Secondary controller not ready to take control. There is a predefined default discrete Logix tag-based alarm for the status. Set standard configuration members of the discrete Logix tag-based alarm. Alarm elements can be accessed as follows: D4SDTag.@Alarms.Alm_Fail.AlarmElement. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_RdyAck | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is ready to be acknowledged. | Read Only | 0 | 0
raP_Dvc_LgxRedun | Sts_RdyReset | Output | BOOL | ORdy_Reset | 0 | Decimal | 0 | 0 | 1 = A latched alarm or shed condition is ready to be reset. | Read Only | 0 | 0
raP_Dvc_LgxRedun | XRdy_Sync | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Sync. | Read Only | 0 | 0
raP_Dvc_LgxRedun | XRdy_Switchover | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Switchover. | Read Only | 0 | 0
raP_Dvc_LgxRedun | XRdy_Reset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Reset, enable button. | Read Only | 0 | 0
raP_Dvc_LgxRedun | XRdy_ResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ResetAckAll, enable button. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Out_Reset | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Reset command has been received and accepted. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Val_Rate | Output | REAL |  | 0 | Float | 0 | 1 | Configured Task Period (milliseconds). | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Val_Priority | Output | DINT |  | 0 | Decimal | 0 | 1 | Configured Task Priority (1..15, lower number is higher priority). | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Val_LastExecTime | Output | REAL |  | 0 | Float | 0 | 1 | Actual Last Execution Time of Task (milliseconds). | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Val_MaxExecTime | Output | REAL |  | 0 | Float | 0 | 1 | Highest Execution Time of Task (milliseconds). | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Val_OverlapCount | Output | DINT |  | 0 | Decimal | 0 | 1 | Task overlap count. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Val_WatchdogTime | Output | REAL |  | 0 | Float | 0 | 1 | Configured Task watchdog timer value (milliseconds). | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Sts_Initialized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Instruction is initialized. Use Inp_InitializeReq to reinitialize. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Sts_TaskInhibited | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = This Task is Inhibited, 0 = this Task is Active. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Sts_eFault | Output | SINT |  | 0 | Decimal | 0 | 0 | Device Fault Status 0 = None, 30 = Task execution time over plan, 34 = Configuration error. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Sts_eNotify | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Sts_eNotifyAll | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values including related objects: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Sts_eNotifyOverPlan | Output | SINT |  | 0 | Decimal | 0 | 0 | Task execution time over plan alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Sts_UnackAlmCount | Output | DINT |  | 0 | Decimal | 0 | 0 | Count of Unacknowledged Alarms. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Error in Configuration, see detail bits (Sts_ErrXxx) for reason. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Sts_ErrAlm | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Error in Logix tag-based alarm settings. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Sts_ErrPlanExecTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Task Planned Exec Time (use 0.1 to 20,000.0 ms) | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Sts_Alm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is active. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Sts_AlmInh | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is shelved or disabled. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Sts_OverPlan | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Task execution time exceeds plan. There is a predefined default discrete Logix tag-based alarm for the status. Set standard configuration members of the discrete Logix tag-based alarm. Alarm elements can be accessed as follows: D4SDTag.@Alarms.Alm_Fail.AlarmElement. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Sts_RdyAck | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is ready to be acknowledged. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | Sts_RdyReset | Output | BOOL | ORdy_Reset | 0 | Decimal | 0 | 0 | 1 = A latched alarm or shed condition is ready to be reset. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | XRdy_Reset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Reset, enable button. | Read Only | 0 | 0
raP_Dvc_LgxTaskMon | XRdy_ResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ResetAckAll, enable button. | Read Only | 0 | 0
raP_Opr_ArbitrationQ | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Opr_ArbitrationQ | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An error exists, see detail bits for reason. | Read/Write | 0 | 0
raP_Opr_ArbitrationQ | Sts_ErrOperClass | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Operator class existence error. | Read/Write | 0 | 0
raP_Opr_ArbitrationQ | Sts_ErrProgClass | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Program class existence error. | Read/Write | 0 | 0
raP_Opr_ArbitrationQ | Sts_ErrExtClass | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = External class existence error. | Read/Write | 0 | 0
raP_Opr_ArbitrationQ | Sts_ErrMaintClass | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Maintenance class existence error. | Read/Write | 0 | 0
raP_Opr_Area | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Opr_Area | Out_ExtddAlmsResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset acknowledge all command to extended alarms. | Read Only | 0 | 0
raP_Opr_Area | Out_ExtddAlmsReset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset command to extended alarms. | Read Only | 0 | 0
raP_Opr_Area | Out_ExtddAlmsDisable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Disable command to extended alarms. | Read Only | 0 | 0
raP_Opr_Area | Out_ExtddAlmsEnable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Enable command to extended alarms. | Read Only | 0 | 0
raP_Opr_Area | Out_ExtddAlmsSuppress | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Suppress command to extended alarms. | Read Only | 0 | 0
raP_Opr_Area | Out_ExtddAlmsUnSuppress | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unsuppress command to extended alarms. | Read Only | 0 | 0
raP_Opr_Area | Out_ExtddAlmsUnShelve | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unshelve command to extended alarms. | Read Only | 0 | 0
raP_Opr_Area | Sts_eSts | Output | SINT |  | 0 | Decimal | 0 | 0 | Area Status: 0 = Powerup / Unknown, 1 = Active, 15 = Out Of service. | Read Only | 0 | 0
raP_Opr_Area | Sts_eFdbk | Output | SINT |  | 0 | Decimal | 0 | 0 | Device Feedback: 0 = Good, 1 = Software Stop, 2 = Emergency Stop. | Read Only | 0 | 0
raP_Opr_Area | Sts_eFault | Output | SINT |  | 0 | Decimal | 0 | 0 | Device Fault Status 0 =None, 5 = Device Alarm, 7 = Extended Alarm, 16 = Not ready trip, 34 = Configuration error. | Read Only | 0 | 0
raP_Opr_Area | Sts_eSrc | Output | INT | CmdSrc.Sts_eSrc | 0 | Decimal | 0 | 0 | The current command source enumerated values: 0 = Logic not in use, 4 = Hand, 8 = Maintenance, 16 = Override, 32 = Program, 33 = Program locked, 34 = Program by default (Normal), 64 = Operator, 65 = Operator locked, 66 = Operator by default (Normal), 128 = Maintenance Out of Service, 129 = Programmed Out of Service (rung false), 256 = External. | Read Only | 0 | 0
raP_Opr_Area | Sts_bSrc | Output | INT | CmdSrc.Sts_bSrc | 0 | Decimal | 0 | 0 | Active selection bitmap (for HMI totem pole with command source request selection): Sts_bSrc.0: hand, Sts_bSrc.1: Programmed Out of service (rung false), Sts_bSrc.2: Maintenance Out of service, Sts_bSrc.3: Maintenance, Sts_bSrc.4: Override, Sts_bSrc.5: External, Sts_bSrc.6: Program locked, Sts_bSrc.7: Program, Sts_bSrc.8: Operator locked, Sts_bSrc.9: Operator. | Read Only | 0 | 0
raP_Opr_Area | Sts_OoS | Output | BOOL | CmdSrc.Sts_OoS | 0 | Decimal | 0 | 0 | 1 = Out of service is selected (supersedes Maintenance, Override, External, Program, Operator). | Read Only | 0 | 0
raP_Opr_Area | Sts_Maint | Output | BOOL | CmdSrc.Sts_Maint | 0 | Decimal | 0 | 0 | 1 = Maintenance is selected (supersedes Override, External, Program, Operator). | Read Only | 0 | 0
raP_Opr_Area | Sts_Ext | Output | BOOL | CmdSrc.Sts_Ext | 0 | Decimal | 0 | 0 | 1 = External is selected (supersedes Program and Operator). | Read Only | 0 | 0
raP_Opr_Area | Sts_Prog | Output | BOOL | CmdSrc.Sts_Prog | 0 | Decimal | 0 | 0 | 1 = Program is selected. | Read Only | 0 | 0
raP_Opr_Area | Sts_ProgLocked | Output | BOOL | CmdSrc.Sts_ProgLocked | 0 | Decimal | 0 | 0 | 1 = Program is selected and locked. | Read Only | 0 | 0
raP_Opr_Area | Sts_Oper | Output | BOOL | CmdSrc.Sts_Oper | 0 | Decimal | 0 | 0 | 1 = Operator is selected. | Read Only | 0 | 0
raP_Opr_Area | Sts_OperLocked | Output | BOOL | CmdSrc.Sts_OperLocked | 0 | Decimal | 0 | 0 | 1 = Operator is selected and locked. | Read Only | 0 | 0
raP_Opr_Area | Sts_ProgOperSel | Output | BOOL | CmdSrc.Sts_ProgOperSel | 0 | Decimal | 0 | 0 | Program/Operator selection (latch) state: 1 = Program, 0 = Operator. | Read Only | 0 | 0
raP_Opr_Area | Sts_ProgOperLock | Output | BOOL | CmdSrc.Sts_ProgOperLock | 0 | Decimal | 0 | 0 | Program/Operator lock (latch) state, 1 = Locked, 0 = Unlocked. | Read Only | 0 | 0
raP_Opr_Area | Sts_Normal | Output | BOOL | CmdSrc.Sts_Normal | 0 | Decimal | 0 | 0 | 1 = Selection equals the normal (Program or Operator). | Read Only | 0 | 0
raP_Opr_Area | Sts_ExtReqInh | Output | BOOL | CmdSrc.Sts_ExtReqInh | 0 | Decimal | 0 | 0 | 1 = External request inhibited, cannot get to External from current state. | Read Only | 0 | 0
raP_Opr_Area | Sts_ProgReqInh | Output | BOOL | CmdSrc.Sts_ProgReqInh | 0 | Decimal | 0 | 0 | 1 = Program request inhibited, cannot get to Program from current state. | Read Only | 0 | 0
raP_Opr_Area | Sts_MAcqRcvd | Output | BOOL | CmdSrc.Sts_MAcqRcvd | 0 | Decimal | 0 | 0 | 1 = Maintenance acquire command received this scan. | Read Only | 0 | 0
raP_Opr_Area | Sts_Alm | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = An alarm is active. | Read Only | 0 | 0
raP_Opr_Area | Sts_AlmInh | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is shelved, disabled or suppressed, display icon. | Read Only | 0 | 0
raP_Opr_Area | Sts_Available | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Available for control by automation (Program). | Read Only | 0 | 0
raP_Opr_Area | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Area error. Set if any error is active. See detailed error descriptions for individual reasons. | Read Only | 0 | 0
raP_Opr_Area | Sts_ErrAlm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in logix tag-based alarm settings. | Read Only | 0 | 0
raP_Opr_Area | Sts_EStop | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Emergency stop ok. | Read Only | 0 | 0
raP_Opr_Area | Sts_EStopTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Area tripped by an EStop not ok. | Read Only | 0 | 0
raP_Opr_Area | Sts_SStop | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Software stop ok. | Read Only | 0 | 0
raP_Opr_Area | Sts_SStopTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Area tripped by SStop not ok. | Read Only | 0 | 0
raP_Opr_Area | Sts_ExtddAlms | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An extended alarm is active. | Read Only | 0 | 0
raP_Opr_Area | Sts_ExtddAlmsAlmInh | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Extended alarm is shelved, disabled or suppressed. | Read Only | 0 | 0
raP_Opr_Area | Sts_ExtddAlmsAlarmFault | Output | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | Alarm fault extended alarm is present. Each bit represents an individual alarm (0 - 31). | Read Only | 0 | 0
raP_Opr_Area | Sts_ExtddAlmsRdyReset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A latched extended alarm is ready to be reset. | Read Only | 0 | 0
raP_Opr_Area | Sts_ExtddAlmsShelved | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A shelved extended alarm is present. | Read Only | 0 | 0
raP_Opr_Area | Sts_ExtddAlmsSuppressed | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A suppressed extended alarm is present. | Read Only | 0 | 0
raP_Opr_Area | Sts_ExtddAlmsDisabled | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A disabled extended alarm is present. | Read Only | 0 | 0
raP_Opr_Area | Sts_ExtddAlmsUnAckd | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An unacknowledged extended alarm is present. | Read Only | 0 | 0
raP_Opr_Area | Sts_ExtddAlmCount | Output | SINT |  | 0 | Decimal | 0 | 0 | Number of extended alarms connected. | Read Only | 0 | 0
raP_Opr_Area | Sts_ExtddAlmsDspl | Output | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | Extended alarm is present for active display, bit (0 - 31). | Read Only | 0 | 0
raP_Opr_Area | Sts_ChildrenGood | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = All children are owned and organized. | Read Only | 0 | 0
raP_Opr_Area | Sts_ChildrenOrganized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = All children are organized. | Read Only | 0 | 0
raP_Opr_Area | Sts_ChildrenOwned | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = All children are owned. | Read Only | 0 | 0
raP_Opr_Area | Sts_ChildrenUnBound | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Children ownership unbound. | Read Only | 0 | 0
raP_Opr_Area | Sts_ExtddAlmMaxCount | Output | SINT |  | 0 | Decimal | 0 | 0 | Indicates the maximum extended alarm active and connected to the object. | Read Only | 0 | 0
raP_Opr_Area | Sts_Initialized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Instruction is initialized. Use Inp_InitializeReq to reinitialize. | Read Only | 0 | 0
raP_Opr_Area | Sts_NotRdy | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Area is not ready, see detail bits (Sts_Nrdyxxx) for reason. | Read Only | 0 | 0
raP_Opr_Area | Sts_NrdyCfgErr | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Area is not ready: configuration error. | Read Only | 0 | 0
raP_Opr_Area | Sts_NrdyChildAlm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Area is not ready: child object alarm. | Read Only | 0 | 0
raP_Opr_Area | Sts_NrdyChildNrdy | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Area is not ready: child object not ready. | Read Only | 0 | 0
raP_Opr_Area | Sts_NrdyEStopTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Area is not ready: emergency stop not ok. | Read Only | 0 | 0
raP_Opr_Area | Sts_NrdyExtddAlms | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Area is not ready: extended alarms not ok. | Read Only | 0 | 0
raP_Opr_Area | Sts_NrdyOoS | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Area is not ready: object disabled by Maintenance. | Read Only | 0 | 0
raP_Opr_Area | Sts_NrdySStopTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Area is not ready: software stop not ok. | Read Only | 0 | 0
raP_Opr_Area | Sts_NrdyChildNotUsable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A child is not usable | Read/Write | 0 | 0
raP_Opr_Area | Sts_Owned | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Child ownership acquired. | Read Only | 0 | 0
raP_Opr_Area | Sts_RdyAck | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is ready to be acknowledged. | Read Only | 0 | 0
raP_Opr_Area | Sts_RdyReset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A latched alarm or shed condition is ready to be reset. | Read Only | 0 | 0
raP_Opr_Area | Sts_Virtual | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = The instruction treats the object as virtual. The instruction acts as normal but the output is kept de-energized (Out_ = 0). 0 = the instruction operates the object normally. | Read Only | 0 | 0
raP_Opr_Area | Sts_eNotify | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Area | Sts_eNotifyAll | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values including related valves: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Area | Sts_eNotifyEStopTrip | Output | SINT |  | 0 | Decimal | 0 | 0 | Emergency stop alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Area | Sts_eNotifySStopTrip | Output | SINT |  | 0 | Decimal | 0 | 0 | Software stop alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Area | Sts_eNotifyExtddAlms | Output | SINT |  | 0 | Decimal | 0 | 0 | Extended alarms status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Area | Sts_UnackAlmCount | Output | SINT |  | 0 | Decimal | 0 | 0 | Count of unacknowledged alarms. | Read Only | 0 | 0
raP_Opr_Area | Sts_UnqID | Output | DINT |  | 0 | Decimal | 0 | 0 | HMI bus object index. | Read Only | 0 | 0
raP_Opr_Area | SrcQ_IO | Output | SINT |  | 0 | Decimal | 0 | 0 | Source and quality of primary input or output (enumerated): 0=Good, live, confirmed good 1=Good, live, assumed good 2=Good, no feedback, assumed good 8=Test, virtualized 9=Test, loopback 10=Test, manually entered 16=Uncertain, live, off-spec 17=Uncertain, substituted at device or bus 18=Uncertain, substituted at instruction 19=Uncertain, using last known good 20=Uncertain, using replacement value 32=Bad, signal failure 33=Bad, channel fault 34=Bad, module or communication fault 35=Bad, invalid configuration | Read Only | 0 | 0
raP_Opr_Area | XRdy_Acq | Output | BOOL | CmdSrc.XRdy_Acq | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Acq, enable HMI button. | Read Only | 0 | 0
raP_Opr_Area | XRdy_Rel | Output | BOOL | CmdSrc.XRdy_Rel | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Rel, enable HMI button. | Read Only | 0 | 0
raP_Opr_Area | XRdy_OwnerAcq | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_OwnerAcq, enable HMI button. | Read Only | 0 | 0
raP_Opr_Area | XRdy_OwnerRel | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_OwnerRel, enable HMI button. | Read Only | 0 | 0
raP_Opr_Area | XRdy_Reset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Reset, enable button. | Read Only | 0 | 0
raP_Opr_Area | XRdy_ResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ResetAckAll, enable button. | Read Only | 0 | 0
raP_Opr_EMGen | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Opr_EMGen | Out_OwnerSts | Output | DINT |  | 0 | Decimal | 0 | 0 | Status of command source, owner command handshake and ready status. 0 = None,.10 = Operator Lock,.11 = Operator Unlock,.12 = Program Lock,.13 = Program Unlock,.14 = Acquire Maintenance,.15 = Release Maintenance,.16 = Acquire External,.17 = Release External,.18 = Has Maintenance,.19 = External Override Lock, .20 = Has External,.21 = Has Operator, .22 = Has Operator Locked, .23 = Has Program, .24 = Has Program Locked, .29 = Echo, .30 = Not Ready. | Read Only | 0 | 0
raP_Opr_EMGen | Out_ExtddAlmsReset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset command to extended alarms. | Read Only | 0 | 0
raP_Opr_EMGen | Out_ExtddAlmsResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset acknowledge all command to extended alarms. | Read Only | 0 | 0
raP_Opr_EMGen | Out_ExtddAlmsDisable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Disable command to extended alarms. | Read Only | 0 | 0
raP_Opr_EMGen | Out_ExtddAlmsEnable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Enable command to extended alarms. | Read Only | 0 | 0
raP_Opr_EMGen | Out_ExtddAlmsSuppress | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Suppress command to extended alarms. | Read Only | 0 | 0
raP_Opr_EMGen | Out_ExtddAlmsUnSuppress | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unsuppress command to extended alarms. | Read Only | 0 | 0
raP_Opr_EMGen | Out_ExtddAlmsUnShelve | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unshelve command to extended alarms. | Read Only | 0 | 0
raP_Opr_EMGen | Ref_SMCfgPath | Output | BOOL |  | 0 | Decimal | 0 | 0 | Populate the Description field for the path to the configuration UDT instance for the HMI | Read Only | 0 | 0
raP_Opr_EMGen | Sts_bSrc | Output | INT | CmdSrc.Sts_bSrc | 0 | Decimal | 0 | 0 | Active selection bitmap (for HMI totem pole with command source request selection): Sts_bSrc.0: hand, Sts_bSrc.1: Programmed Out of service (rung false), Sts_bSrc.2: Maintenance Out of service, Sts_bSrc.3: Maintenance, Sts_bSrc.4: Override, Sts_bSrc.5: External, Sts_bSrc.6: Program locked, Sts_bSrc.7: Program, Sts_bSrc.8: Operator locked, Sts_bSrc.9: Operator. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_eSrc | Output | INT | CmdSrc.Sts_eSrc | 0 | Decimal | 0 | 0 | The current command source enumerated values: 0 = Logic not in use, 4 = Hand, 8 = Maintenance, 16 = Override, 32 = Program, 33 = Program locked, 34 = Program by default (Normal), 64 = Operator, 65 = Operator locked, 66 = Operator by default (Normal), 128 = Maintenance Out of Service, 129 = Programmed Out of Service (rung false), 256 = External. | Read Only | 0 | 0
raP_Opr_EMGen | Sts | Output | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | State Status (bitwise). | Read Only | 0 | 0
raP_Opr_EMGen | Sts_Rqst | Output | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | Program State Request (bitwise). | Read Only | 0 | 0
raP_Opr_EMGen | Sts_StateCompleteRqst | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = State complete request. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_eCmd | Output | SINT |  | 0 | Decimal | 0 | 0 | Device Command Bit 0 = Command 1, Bit 1 = Command 2, Bit 2 = Command 3, Bit 3 = Command 4, ... Bit 31 = Command 32. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_eFault | Output | SINT |  | 0 | Decimal | 0 | 0 | Device Fault Status 0 = None, 5 = Device Alarm, 7 = External Alarm, 15 = Interlock trip, 16 = Not ready trip, 34 = Configuration Error. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ePrevState | Output | DINT |  | 0 | Decimal | 0 | 0 | The last active state (bitwise). | Read Only | 0 | 0
raP_Opr_EMGen | Sts_eRestartState | Output | DINT |  | 0 | Decimal | 0 | 0 | Restart state (bitwise). | Read Only | 0 | 0
raP_Opr_EMGen | Sts_eState | Output | DINT |  | 0 | Decimal | 0 | 1 | Equipment module process state. (x) This value represents equipment module process state (bitwise). | Read Only | 0 | 0
raP_Opr_EMGen | Sts_eStep | Output | INT |  | 0 | Decimal | 0 | 1 | Equipment module process step. This value represents equipment module process step. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_eSts | Output | DINT |  | 0 | Decimal | 0 | 1 | Equipment module state. This value represents equipment module state. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_eSummary | Output | INT |  | 0 | Decimal | 0 | 0 | Actual process summary. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_eNotify | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_eNotifyAll | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values including related valves: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_eNotifyDvcAlms | Output | SINT |  | 0 | Decimal | 0 | 0 | Device alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_eNotifyExtddAlms | Output | SINT |  | 0 | Decimal | 0 | 0 | Extended alarms status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_eNotifyIntlkTrip | Output | SINT |  | 0 | Decimal | 0 | 0 | Interlock trip alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_eNotifyRptData | Output | SINT |  | 0 | Decimal | 0 | 0 | Report data alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ExtddAlmCount | Output | SINT |  | 0 | Decimal | 0 | 0 | Number of extended alarms connected. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_UnackAlmCount | Output | SINT |  | 0 | Decimal | 0 | 0 | Count of unacknowledged alarms. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_Idle | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Idle State. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_Alm | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = An alarm is active. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_AlmInh | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is shelved, disabled or suppressed, display icon. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_Available | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Available for control by automation (Program). | Read Only | 0 | 0
raP_Opr_EMGen | Sts_BypActive | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Bypassing active (Bypassed or Maintenance). | Read Only | 0 | 0
raP_Opr_EMGen | Sts_Bypass | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Bypassable interlocks and permissives are bypassed. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_MaintByp | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment module has a maintenance bypass function active. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_DvcAlms | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device alarms ok. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Equipment module error. Set if any error is active. See detailed error descriptions for individual reasons. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ErrAlm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in logix tag-based alarm settings. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ErrLimPar | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Scaled EU Min = Max. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ErrPSetPar | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: PSet is invalid. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ErrTypePar | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: No In/Out Parameter Assigned. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ErrLimRpt | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Scaled EU Min = Max. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ErrPSetRpt | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: PSet is invalid. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ErrTypeRpt | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: No In/Out Parameter Assigned. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ExtddAlms | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An extended alarm is active. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ExtddAlmsAlmInh | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Extended alarm is shelved, disabled or suppressed. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ExtddAlmsAlarmFault | Output | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | Alarm fault extended alarm is present. Each bit represents an individual alarm (0 - 31). | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ExtddAlmsDspl | Output | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | Extended alarm is present for active display (0 - 31). | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ExtddAlmsRdyReset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A latched extended alarm is ready to be reset. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ExtddAlmsShelved | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A shelved extended alarm is present. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ExtddAlmsSuppressed | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A suppressed extended alarm is present. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ExtddAlmsDisabled | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A disabled extended alarm is present. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ExtddAlmsUnAckd | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An unacknowledged extended alarm is present. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ExtddAlmMaxCount | Output | SINT |  | 0 | Decimal | 0 | 0 | Indicates the maximum extended alarm active and connected to the object. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ChildrenGood | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = All children are owned and organized. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ChildrenOrganized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = All children are organized. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ChildrenOwned | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = All children are owned. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ChildrenUnBound | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Children ownership unbound. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_IntlkAvailable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment module can be acquired by Program and is available for start/stop control when interlocks are ok. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_IntlkTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment module tripped by an interlock not ok. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_GroupIntlkOk | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Group Interlock ok. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_GroupPermOk | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Group Permissive ok. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_HasVSM | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Has associated raP_VSM. Configurable State Machine 32 Max States 32 Max Commands | Read/Write | 0 | 0
raP_Opr_EMGen | Sts_NotRdy | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment module is not ready to run (independent of Mode). | Read Only | 0 | 0
raP_Opr_EMGen | Sts_NrdyExtddAlms | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment module is not ready: extended alarms not ok. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ParAdjstd | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Parameter value adjusted. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ParLimFault | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Parameter limit fault. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_RptAdjstd | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Report value adjusted. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_RptLimFault | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Report limit fault. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_SStopTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tripped by a SStop not ok. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_Ext | Output | BOOL | CmdSrc.Sts_Ext | 0 | Decimal | 0 | 0 | 1 = External is selected (supersedes Program and Operator). | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ExtReqInh | Output | BOOL | CmdSrc.Sts_ExtReqInh | 0 | Decimal | 0 | 0 | 1 = External request inhibited, cannot get to External from current state. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_MAcqRcvd | Output | BOOL | CmdSrc.Sts_MAcqRcvd | 0 | Decimal | 0 | 0 | 1 = Maintenance acquire command received this scan. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_Maint | Output | BOOL | CmdSrc.Sts_Maint | 0 | Decimal | 0 | 1 | 1 = Maintenance is selected (supersedes Override, External, Program, Operator). | Read Only | 0 | 0
raP_Opr_EMGen | Sts_Normal | Output | BOOL | CmdSrc.Sts_Normal | 0 | Decimal | 0 | 0 | 1 = Selection equals the normal (Program or Operator). | Read Only | 0 | 0
raP_Opr_EMGen | Sts_OoS | Output | BOOL | CmdSrc.Sts_OoS | 0 | Decimal | 0 | 0 | 1 = Out of service is selected (supersedes Maintenance, Override, External, Program, Operator). | Read Only | 0 | 0
raP_Opr_EMGen | Sts_Oper | Output | BOOL | CmdSrc.Sts_Oper | 0 | Decimal | 0 | 1 | 1 = Operator is selected. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_OperLocked | Output | BOOL | CmdSrc.Sts_OperLocked | 0 | Decimal | 0 | 0 | 1 = Operator is selected and locked. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_Prog | Output | BOOL | CmdSrc.Sts_Prog | 0 | Decimal | 0 | 1 | 1 = Program is selected. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ProgLocked | Output | BOOL | CmdSrc.Sts_ProgLocked | 0 | Decimal | 0 | 0 | 1 = Program is selected and locked. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ProgOperLock | Output | BOOL | CmdSrc.Sts_ProgOperLock | 0 | Decimal | 0 | 0 | Program/Operator lock (latch) state, 1 = Locked, 0 = Unlocked. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ProgOperSel | Output | BOOL | CmdSrc.Sts_ProgOperSel | 0 | Decimal | 0 | 0 | Program/Operator selection (latch) state: 1 = Program, 0 = Operator. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ProgReqInh | Output | BOOL | CmdSrc.Sts_ProgReqInh | 0 | Decimal | 0 | 0 | 1 = Program request inhibited, cannot get to Program from current state. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_Initialized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Instruction is initialized. Use Inp_InitializeReq to reinitialize. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_NrdyCfgErr | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment module is not ready: configuration error. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_NrdyChildAlm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment module is not ready: child object alarm. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_NrdyChildNrdy | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment module is not ready: child object not ready. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_NrdyOoS | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment module is not ready: object disabled by Maintenance. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_NrdyPerm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment module is not ready: permissive not ok. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_NrdyGroupPerm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment phase is not ready: group permissive not ok. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_NrdySStopTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment module is not ready: software stop not ok. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_NrdyIntlk | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment module is not ready: interlock not ok. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_NrdyGroupIntlk | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment phase is not ready: group interlock not ok. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_NrdyChildNotUsable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A child is not usable | Read/Write | 0 | 0
raP_Opr_EMGen | Sts_Owned | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Child ownership acquired. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_RdyAck | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is ready to be acknowledged. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_RdyReset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A latched alarm or shed condition is ready to be reset. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ParCapture | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Capture Initial parameter setting. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ParClear | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Clear parameter setting. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_RptCapture | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Capture initial report setting. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_RptClear | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Clear report setting. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_ParRestore | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Restore initial report setting. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_RptRestore | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Restore initial report setting. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_CompleteRptTrgr | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Complete report data trigger. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_RptData | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Report data alarm. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_StartRptTrgr | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Start report trigger. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_Req | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment module transition from idle state to any other active equipment module state. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_PromptActive | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Prompt Active | Read Only | 0 | 0
raP_Opr_EMGen | Sts_UserDINT1 | Output | DINT |  | 0 | Decimal | 0 | 0 | User Definable DINT Output 1. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_UserDINT2 | Output | DINT |  | 0 | Decimal | 0 | 0 | User Definable DINT Output 2. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_UserReal1 | Output | REAL |  | 0 | Float | 0 | 0 | User Definable Real Output 1. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_UserReal2 | Output | REAL |  | 0 | Float | 0 | 0 | User Definable Real Output 2. | Read Only | 0 | 0
raP_Opr_EMGen | Sts_UnqID | Output | DINT |  | 0 | Decimal | 0 | 0 | HMI bus object index. | Read Only | 0 | 0
raP_Opr_EMGen | Val_ActlStep | Output | INT |  | 0 | Decimal | 0 | 1 | Actual process step number. | Read Only | 0 | 0
raP_Opr_EMGen | Val_PrevStep | Output | INT |  | 0 | Decimal | 0 | 0 | The last active process step number. | Read Only | 0 | 0
raP_Opr_EMGen | Val_ReturnStateNum | Output | SINT |  | 0 | Decimal | 0 | 0 | Return State number | Read Only | 0 | 0
raP_Opr_EMGen | Val_HoldIndx | Output | INT |  | 0 | Decimal | 0 | 0 | Process step hold index to return at Re-Start. | Read Only | 0 | 0
raP_Opr_EMGen | Val_OrganizedStep | Output | INT |  | 0 | Decimal | 0 | 0 | Program setting of process step number. | Read Only | 0 | 0
raP_Opr_EMGen | Val_Owner | Output | DINT |  | 0 | Decimal | 0 | 0 | Owner. The arbitration function within the module arbitrates requests for ownership (.PSet_Owner). The Owner value is used to publish the current owner of the device. | Read Only | 0 | 0
raP_Opr_EMGen | XRdy_Acq | Output | BOOL | CmdSrc.XRdy_Acq | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Acq, enable button. | Read Only | 0 | 0
raP_Opr_EMGen | XRdy_Rel | Output | BOOL | CmdSrc.XRdy_Rel | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Rel, enable button. | Read Only | 0 | 0
raP_Opr_EMGen | XRdy_OwnerAcq | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_OwnerAcq, enable HMI button. | Read Only | 0 | 0
raP_Opr_EMGen | XRdy_OwnerRel | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_OwnerRel, enable HMI button. | Read Only | 0 | 0
raP_Opr_EMGen | XRdy_ParCapture | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ParCapture, enable button. | Read Only | 0 | 0
raP_Opr_EMGen | XRdy_ParClear | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ParClear, enable button. | Read Only | 0 | 0
raP_Opr_EMGen | XRdy_ParRestore | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ParRestore, enable button. | Read Only | 0 | 0
raP_Opr_EMGen | XRdy_RptCapture | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_RptCapture, enable button. | Read Only | 0 | 0
raP_Opr_EMGen | XRdy_RptClear | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_RptClear, enable button. | Read Only | 0 | 0
raP_Opr_EMGen | XRdy_RptRestore | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_RptRestore, enable button. | Read Only | 0 | 0
raP_Opr_EMGen | XRdy_Reset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Reset, enable button. | Read Only | 0 | 0
raP_Opr_EMGen | XRdy_ResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ResetAckAll, enable button. | Read Only | 0 | 0
raP_Opr_EMGen | XRdy | Output | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Ready for XCmd.(x), enable button. | Read Only | 0 | 0
raP_Opr_EMGen | XRdy_State | Output | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | 1 = Ready for PCmd.(x), enable parameter. | Read Only | 0 | 0
raP_Opr_EPGen | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Opr_EPGen | Out_OwnerSts | Output | DINT |  | 0 | Decimal | 0 | 0 | Status of command source, owner command handshake and ready status. 0 = None,.10 = Operator Lock,.11 = Operator Unlock,.12 = Program Lock,.13 = Program Unlock,.14 = Acquire Maintenance,.15 = Release Maintenance,.16 = Acquire External,.17 = Release External,.18 = Has Maintenance,.19 = External Override Lock, .20 = Has External,.21 = Has Operator, .22 = Has Operator Locked, .23 = Has Program, .24 = Has Program Locked, .29 = Echo, .30 = Not Ready. | Read Only | 0 | 0
raP_Opr_EPGen | Out_ExtddAlmsReset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset command to extended alarms. | Read Only | 0 | 0
raP_Opr_EPGen | Out_ExtddAlmsResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset acknowledge all command to extended alarms. | Read Only | 0 | 0
raP_Opr_EPGen | Out_ExtddAlmsDisable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Disable command to extended alarms. | Read Only | 0 | 0
raP_Opr_EPGen | Out_ExtddAlmsEnable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Enable command to extended alarms. | Read Only | 0 | 0
raP_Opr_EPGen | Out_ExtddAlmsSuppress | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Suppress command to extended alarms. | Read Only | 0 | 0
raP_Opr_EPGen | Out_ExtddAlmsUnSuppress | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unsuppress command to extended alarms. | Read Only | 0 | 0
raP_Opr_EPGen | Out_ExtddAlmsUnShelve | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unshelve command to extended alarms. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Idle | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Idle. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Running | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Running. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Stopped | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Stopped. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Stopping | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Stopping. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Holding | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Holding. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Held | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Held. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Restarting | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Restarting. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Resetting | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Resetting. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Aborting | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Aborting. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Aborted | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Aborted. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Pausing | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Pausing. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Paused | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Paused. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_PauseEnabled | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Pause enabled. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_AutoPauseEnabled | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Auto paused enabled. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Complete | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Running complete. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_CompleteRptTrgr | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Complete report data trigger. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_StartRqst | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Start request. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_StopRqst | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Stop Request. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_HoldRqst | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Hold Request. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_RestartRqst | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Restart request. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_AbortRqst | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Abort request. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_PauseRqst | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Pause Request. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_AutoPauseRqst | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Auto pause request. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ResumeRqst | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Resume from paused request. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_StateCompleteRqst | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = State complete request. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_MapAlmToPhs | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Map alarm codes from Equipment phase to the Phase PFL codes. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_OnlyHoldEP | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = When a hold request is received from the HMI, Only hold the Equipment phase, do not inform FTBatch. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ExtSeq | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = This Phase has an External Sequencer Associated to it (FTBatch). | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Req | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Phase transition from idle state to any other active phase state. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_PhsOwnerExtlSeq | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A PC-based application that commands the equipment phase via CIP messages. Other sequencers can’t give commands to the equipment phase. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_PhsOwnerIntlSeq | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A Logix program that uses instructions to command the equipment phase. Other sequencers can’t give commands to the equipment phase. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_PhsOwnerLogix | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = The command toolbar and phase monitor window send commands to the equipment phase. Sequencers can’t give commands to the equipment phase. This includes Internal and External. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_StartRptTrgr | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Start report trigger. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_bSrc | Output | INT | CmdSrc.Sts_bSrc | 0 | Decimal | 0 | 0 | Active selection bitmap (for HMI totem pole with command source request selection): Sts_bSrc.0: hand, Sts_bSrc.1: Programmed Out of service (rung false), Sts_bSrc.2: Maintenance Out of service, Sts_bSrc.3: Maintenance, Sts_bSrc.4: Override, Sts_bSrc.5: External, Sts_bSrc.6: Program locked, Sts_bSrc.7: Program, Sts_bSrc.8: Operator locked, Sts_bSrc.9: Operator. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_eSrc | Output | INT | CmdSrc.Sts_eSrc | 0 | Decimal | 0 | 0 | The current command source enumerated values: 0 = Logic not in use, 4 = Hand, 8 = Maintenance, 16 = Override, 32 = Program, 33 = Program locked, 34 = Program by default (Normal), 64 = Operator, 65 = Operator locked, 66 = Operator by default (Normal), 128 = Maintenance Out of Service, 129 = Programmed Out of Service (rung false), 256 = External. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_eCmd | Output | SINT |  | 0 | Decimal | 0 | 0 | Device Command 0 = None 2 = Run 3 = Complete 4 = Hold 6 = ReStart 7 = Stop 9 = Abort 11 = Pause 12 = Auto Pause 13 = ReSet 14 = Resume. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_eFault | Output | SINT |  | 0 | Decimal | 0 | 0 | Device Fault Status 0 = None, 5 = Device Alarm, 7 = External Alarm, 15 = Interlock trip, 16 = Not ready trip, 34 = Configuration Error. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_eAttchRslts | Output | DINT |  | 0 | Decimal | 0 | 0 | Phase attach (Ownership) results. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_eCmmndRslts | Output | DINT |  | 0 | Decimal | 0 | 0 | Phase command results. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ePhsOwner | Output | DINT |  | 0 | Decimal | 0 | 1 | Shows the current owner(s) of the Equipment Phase. Available owners are: Internal Sequencer External Sequencer Operator Logix Designer (#) - where # is a count of separate Logix Designer applications overriding ownership. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ePhsState | Output | DINT |  | 0 | Decimal | 0 | 1 | Current State. This value stores the current state of the Equipment phase’s associated Equipment Phase as a bit pattern. This is a direct mapping of the Phase. State register. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_eState | Output | DINT |  | 0 | Decimal | 0 | 1 | Equipment phase process state. 0 = ? 1 = Idle 2 = Running 3 = Complete 4 = Holding 5 = Held 6 = ReStarting 7 = Stopping 8 = Stopped 9 = Aborting 10 = Aborted 11 = Pausing 12 = Paused 13 = ReSetting. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ePrevState | Output | DINT |  | 0 | Decimal | 0 | 0 | The last Active State. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_eStep | Output | INT |  | 0 | Decimal | 0 | 1 | Equipment phase process step. This value represents equipment phase process step. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_eSts | Output | SINT |  | 0 | Decimal | 0 | 1 | Equipment Phase status: 0 = ? 1 = Idle 2 = Running 3 = Complete 4 = Holding 5 = Held 6 = ReStarting 7 = Stopping 8 = Stopped 9 = Aborting 10 = Aborted 11 = Pausing 12 = Paused 13 = ReSetting 33 = Out of service. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_eSummary | Output | INT |  | 0 | Decimal | 0 | 0 | Actualf process summary. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_eNotifyAll | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values including related valves: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_eNotify | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_eNotifyDvcAlms | Output | SINT |  | 0 | Decimal | 0 | 0 | Device alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_eNotifyExtddAlms | Output | SINT |  | 0 | Decimal | 0 | 0 | Extended alarms status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_eNotifyIntlkTrip | Output | SINT |  | 0 | Decimal | 0 | 0 | Interlock trip alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_eNotifyRptData | Output | SINT |  | 0 | Decimal | 0 | 0 | Report data alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_UnackAlmCount | Output | SINT |  | 0 | Decimal | 0 | 0 | Count of unacknowledged alarms. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Alm | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = An alarm is active. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_AlmInh | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is shelved, disabled or suppressed, display icon. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Available | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Available for control by automation (Program). | Read Only | 0 | 0
raP_Opr_EPGen | Sts_BypActive | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Bypassing active (Bypassed or Maintenance). | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Bypass | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Bypassable interlocks and permissives are bypassed. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_MaintByp | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment phase has a maintenance bypass function active. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_CompleteONS | Output | BOOL |  | 0 | Decimal | 0 | 0 | Phase complete, stopped or aborted oneshot. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_DvcAlms | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Device alarms ok. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Equipment phase error. Set if any error is active. See detailed error descriptions for individual reasons. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ErrAlm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in logix tag-based alarm settings. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ErrLimPar | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Scaled EU Min = Max. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ErrLimRpt | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Scaled EU Min = Max. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ErrPSetPar | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: PSet is invalid. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ErrPSetRpt | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: PSet is invalid. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ErrTypePar | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: No In/Out Parameter Assigned. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ErrTypeRpt | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: No In/Out Parameter Assigned. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ExtddAlms | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An extended alarm is active. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ExtddAlmsAlmInh | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Extended alarm is shelved, disabled or suppressed. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ExtddAlmsAlarmFault | Output | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | Alarm fault extended alarm is present. Each bit represents an individual alarm (0 - 31). | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ExtddAlmsRdyReset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A latched extended alarm is ready to be reset. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ExtddAlmsShelved | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A shelved extended alarm is present. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ExtddAlmsSuppressed | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A suppressed extended alarm is present. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ExtddAlmsDisabled | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A disabled extended alarm is present. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ExtddAlmsUnAckd | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An unacknowledged extended alarm is present. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_NotRdy | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment phase is not ready to run (independent of Mode). | Read Only | 0 | 0
raP_Opr_EPGen | Sts_NrdyExtddAlms | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment phase is not ready: extended alarms not ok. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_NrdyCfgErr | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment phase is not ready: configuration error. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_NrdyChildAlm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment phase is not ready: child object alarm. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_NrdyChildNrdy | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment phase is not ready: child object not ready. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_NrdyIntlk | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment phase is not ready: interlock not ok. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_NrdyGroupIntlk | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment phase is not ready: group interlock not ok. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_NrdyOoS | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment phase is not ready: object disabled by Maintenance. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_NrdyPerm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment phase is not ready: permissive not ok. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_NrdyGroupPerm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment phase is not ready: group permissive not ok. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_NrdySStopTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment phase is not ready: software stop not ok. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_NrdyChildNotUsable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A child is not usable | Read/Write | 0 | 0
raP_Opr_EPGen | Sts_ParAdjstd | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Parameter value adjusted. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ParCapture | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Capture Initial parameter setting. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ParClear | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Clear parameter setting. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ParLimFault | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Parameter limit fault. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ParRestore | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Restore initial report setting. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ResetRqst | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset phase request. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_RptAdjstd | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Report value adjusted. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_RptLimFault | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Report limit fault. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_SStopTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Tripped by a SStop not ok. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_UserReal1 | Output | REAL |  | 0 | Float | 0 | 0 | User Definable Real Output 1. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_UserReal2 | Output | REAL |  | 0 | Float | 0 | 0 | User Definable Real Output 2. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_UserDINT1 | Output | DINT |  | 0 | Decimal | 0 | 0 | User Definable DINT Output 1. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_UserDINT2 | Output | DINT |  | 0 | Decimal | 0 | 0 | User Definable DINT Output 2. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ExtddAlmCount | Output | SINT |  | 0 | Decimal | 0 | 0 | Number of extended alarms connected. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ExtddAlmsDspl | Output | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | Extended alarm is present for active display. Bit (0 - 31). | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ExtddAlmMaxCount | Output | SINT |  | 0 | Decimal | 0 | 0 | Indicates the maximum extended alarm active and connected to the object. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Ext | Output | BOOL | CmdSrc.Sts_Ext | 0 | Decimal | 0 | 0 | 1 = External is selected (supersedes Program and Operator). | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ExtReqInh | Output | BOOL | CmdSrc.Sts_ExtReqInh | 0 | Decimal | 0 | 0 | 1 = External request inhibited, cannot get to External from current state. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ChildrenGood | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = All children are owned and organized. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ChildrenOrganized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = All children are organized. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ChildrenOwned | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = All children are owned. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ChildrenUnBound | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Children ownership unbound. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_MAcqRcvd | Output | BOOL | CmdSrc.Sts_MAcqRcvd | 0 | Decimal | 0 | 0 | 1 = Maintenance acquire command received this scan. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Maint | Output | BOOL | CmdSrc.Sts_Maint | 0 | Decimal | 0 | 1 | 1 = Maintenance is selected (supersedes Override, External, Program, Operator). | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Normal | Output | BOOL | CmdSrc.Sts_Normal | 0 | Decimal | 0 | 0 | 1 = Selection equals the normal (Program or Operator). | Read Only | 0 | 0
raP_Opr_EPGen | Sts_OoS | Output | BOOL | CmdSrc.Sts_OoS | 0 | Decimal | 0 | 0 | 1 = Out of service is selected (supersedes Maintenance, Override, External, Program, Operator). | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Oper | Output | BOOL | CmdSrc.Sts_Oper | 0 | Decimal | 0 | 1 | 1 = Operator is selected. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_OperLocked | Output | BOOL | CmdSrc.Sts_OperLocked | 0 | Decimal | 0 | 0 | 1 = Operator is selected and locked. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Prog | Output | BOOL | CmdSrc.Sts_Prog | 0 | Decimal | 0 | 1 | 1 = Program is selected. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ProgLocked | Output | BOOL | CmdSrc.Sts_ProgLocked | 0 | Decimal | 0 | 0 | 1 = Program is selected and locked. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ProgOperLock | Output | BOOL | CmdSrc.Sts_ProgOperLock | 0 | Decimal | 0 | 0 | Program/Operator lock (latch) state, 1 = Locked, 0 = Unlocked. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ProgOperSel | Output | BOOL | CmdSrc.Sts_ProgOperSel | 0 | Decimal | 0 | 0 | Program/Operator selection (latch) state: 1 = Program, 0 = Operator. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_ProgReqInh | Output | BOOL | CmdSrc.Sts_ProgReqInh | 0 | Decimal | 0 | 0 | 1 = Program request inhibited, cannot get to Program from current state. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Initialized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Instruction is initialized. Use Inp_InitializeReq to reinitialize. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_IntlkAvailable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment phase can be acquired by Program and is available for start/stop control when interlocks are ok. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_IntlkTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Equipment phase tripped by an interlock not ok. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_GroupIntlkOk | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Group Interlock ok. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_GroupPermOk | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Group Permissive ok. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Owned | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Child ownership acquired. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Active | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Phase synchronization status active. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Done | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Phase synchronization status done. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_Waiting | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Phase synchronization status waiting. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_PromptActive | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Prompt Active | Read Only | 0 | 0
raP_Opr_EPGen | Sts_RptData | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Report data alarm. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_RdyAck | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is ready to be acknowledged. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_RdyReset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A latched alarm or shed condition is ready to be reset. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_RptCapture | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Capture initial report setting. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_RptClear | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Clear report setting. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_RptRestore | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Restore initial report setting. | Read Only | 0 | 0
raP_Opr_EPGen | Sts_UnqID | Output | DINT |  | 0 | Decimal | 0 | 0 | HMI bus object index. | Read Only | 0 | 0
raP_Opr_EPGen | Val_ActlStep | Output | INT |  | 0 | Decimal | 0 | 1 | Actual process step number. | Read Only | 0 | 0
raP_Opr_EPGen | Val_PrevStep | Output | INT |  | 0 | Decimal | 0 | 0 | The last active process step number. | Read Only | 0 | 0
raP_Opr_EPGen | Val_HoldIndx | Output | INT |  | 0 | Decimal | 0 | 1 | Process step hold index to return at Re-Start. | Read Only | 0 | 0
raP_Opr_EPGen | Val_Owner | Output | DINT |  | 0 | Decimal | 0 | 0 | Owner. The arbitration function within the module arbitrates requests for ownership (.PSet_Owner). The Owner value is used to publish the current owner of the device. | Read Only | 0 | 0
raP_Opr_EPGen | Val_OrganizedStep | Input | INT |  | 0 | Decimal | 0 | 0 | Program setting of process step number. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_Acq | Output | BOOL | CmdSrc.XRdy_Acq | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Acq, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_Rel | Output | BOOL | CmdSrc.XRdy_Rel | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Rel, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_OwnerRel | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_OwnerOper, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_OwnerAcq | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_OwnerRel, enable HMI button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_Abort | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Abort, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_AutoPause | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_AutoPause, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_Hold | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Hold, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_ParCapture | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ParCapture, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_ParClear | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ParClear, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_ParRestore | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ParRestore, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_Pause | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Pause, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_RptCapture | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_RptCapture, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_RptClear | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_RptClear, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_RptRestore | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_RptRestore, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_Reset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Reset, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_ResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ResetAckAll, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_ResetPhs | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ResetPhs, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_Restart | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Restart, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_Resume | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Resume, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_Stop | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Stop, enable button. | Read Only | 0 | 0
raP_Opr_EPGen | XRdy_Start | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Start, enable button. | Read Only | 0 | 0
raP_Opr_ExtddAlm | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Opr_ExtddAlm | Out_ExtddAlmDsply | Output | BOOL |  | 0 | Decimal | 1 | 1 | 1 = Extended alarm severity value is greatest of all extended alarms active. Each bit represents an individual alarm (0 - 31). | Read Only | 0 | 0
raP_Opr_ExtddAlm | Used | Output | BOOL |  | 0 | Decimal | 1 | 1 | 1 = Used. | Read Only | 0 | 0
raP_Opr_ExtddAlm | Alm | Output | BOOL |  | 0 | Decimal | 1 | 1 | 1 = Alarm is active. | Read Only | 0 | 0
raP_Opr_ExtddAlm | Acked | Output | BOOL |  | 2#0 | Binary | 1 | 1 | 1 = In alarm unacknowledged. | Read Only | 0 | 0
raP_Opr_ExtddAlm | Disabled | Output | BOOL |  | 2#0 | Binary | 1 | 1 | 1 = Alarm disabled. | Read Only | 0 | 0
raP_Opr_ExtddAlm | Shelved | Output | BOOL |  | 2#0 | Binary | 1 | 1 | 1 = Alarm shelved. | Read Only | 0 | 0
raP_Opr_ExtddAlm | Suppressed | Output | BOOL |  | 2#0 | Binary | 1 | 1 | 1 = Alarm suppressed. | Read Only | 0 | 0
raP_Opr_ExtddAlm | AlarmFault | Output | BOOL |  | 2#0 | Binary | 1 | 1 | 1 = Alarm fault. | Read Only | 0 | 0
raP_Opr_ExtddAlm | Sts_Initialized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Instruction is initialized. Use Inp_InitializeReq to reinitialize. | Read Only | 0 | 0
raP_Opr_ExtddAlm | Sts | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Extended alarm active. | Read Only | 0 | 0
raP_Opr_ExtddAlm | Sts_AlmInh | Output | BOOL |  | 0 | Decimal | 1 | 1 | 1 = One or more alarms shelved, disabled or suppressed. | Read Only | 0 | 0
raP_Opr_ExtddAlm | Sts_RdyReset | Output | BOOL |  | 0 | Decimal | 1 | 1 | 1 = A latched alarm condition is ready to be reset. | Read Only | 0 | 0
raP_Opr_ExtddAlm | Sts_RdyAck | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is ready to be acknowledged. | Read Only | 0 | 0
raP_Opr_ExtddAlm | Sts_eNotify | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_ExtddAlm | XRdy_Reset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Reset, enable button. | Read Only | 0 | 0
raP_Opr_ExtddAlm | XRdy_ResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ResetAckAll, enable button. | Read Only | 0 | 0
raP_Opr_OrgScan | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Opr_OrgScan | Sts_ErrDB | Output | INT |  | 0 | Decimal | 0 | 0 | 1 = Error detected in the Node array structure. | Read Only | 0 | 0
raP_Opr_OrgScan | Sts_Empty | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = The Node array is currently empty. | Read/Write | 0 | 0
raP_Opr_OrgScan | Sts_Full | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = The Node array is currently full. | Read/Write | 0 | 0
raP_Opr_OrgScan | Sts_EditAdd | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An Add was just executed (single scan). | Read/Write | 0 | 0
raP_Opr_OrgScan | Sts_EditDel | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A delete was just executed (single scan). | Read/Write | 0 | 0
raP_Opr_OrgScan | Sts_Edit | Output | DINT |  | 0 | Decimal | 0 | 0 | Node number involved in last edit. | Read/Write | 0 | 0
raP_Opr_OrgScan | ORdy_AddChild | Output | BOOL |  | 0 | Decimal | 0 | 0 | Selections allow for node child addition. 1 = Ready for OCmd_AddChild, enable HMI button. | Read/Write | 0 | 0
raP_Opr_OrgScan | ORdy_DelNode | Output | BOOL |  | 0 | Decimal | 0 | 0 | Selections allow node deletion. 1 = Ready for OCmd_DelNode, enable HMI button. | Read/Write | 0 | 0
raP_Opr_OrgScan | ORdy_SetBus | Output | BOOL |  | 0 | Decimal | 0 | 0 | Selections allow Bus assignment to a node. 1 = Ready for OCmd_SetBus, enable HMI button. | Read/Write | 0 | 0
raP_Opr_OrgView | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Opr_OrgView | Sts_IsEditor | Output | BOOL |  | 0 | Decimal | 0 | 0 | Status, 1 = is the organization editor. | Read/Write | 0 | 0
raP_Opr_OrgView | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 0 | Configuration Error. | Read/Write | 0 | 0
raP_Opr_OrgView | Sts_CfgErr | Output | BOOL |  | 0 | Decimal | 0 | 0 | Node array size exceeds limit | Read Only | 0 | 0
raP_Opr_Owner | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Opr_Owner | Out_OwnerCmd | Output | DINT |  | 0 | Decimal | 0 | 0 | Output to issue commands to the associated CmdSrc | Read Only | 0 | 0
raP_Opr_Owner | Sts_HasArb | Output | SINT | Wrk_HasArb | 0 | Decimal | 0 | 0 | Bit mapped status of arbitration queue existence by class. | Read Only | 0 | 0
raP_Opr_Owner | Sts_AFull | Output | SINT | Wrk_AFull | 0 | Decimal | 0 | 0 | Bit mapped status of arbitration queue full by class. | Read Only | 0 | 0
raP_Opr_Owner | Sts_HasClass | Output | SINT | Wrk_HasClass | 0 | Decimal | 0 | 0 | Bit mapped status of class existence. | Read Only | 0 | 0
raP_Opr_Owner | Sts_Owned | Output | BOOL |  | 0 | Decimal | 0 | 1 | Status that this object is owned. | Read Only | 0 | 0
raP_Opr_Owner | Sts_OwnedInv | Output | BOOL |  | 0 | Decimal | 0 | 0 | Inversion of the Sts_Owned. | Read Only | 0 | 0
raP_Opr_Owner | Sts_ChildrenOwned | Output | BOOL |  | 0 | Decimal | 0 | 0 |  | Read/Write | 0 | 0
raP_Opr_Owner | Sts_IntOrganized | Output | BOOL |  | 0 | Decimal | 0 | 0 | Status indicating that this object is owned and the associated CmdSrc is in the correct state | Read Only | 0 | 0
raP_Opr_Owner | Sts_ChildrenOrganized | Output | BOOL |  | 0 | Decimal | 0 | 0 | Status indicating that all children are owned and in the correct state | Read Only | 0 | 0
raP_Opr_Owner | Sts_ChildrenGood | Output | BOOL |  | 0 | Decimal | 0 | 0 |  | Read/Write | 0 | 0
raP_Opr_Owner | Sts_Organized | Output | BOOL |  | 0 | Decimal | 0 | 1 | Sts_IntOrganized AND Sts_ExtOrganized. | Read Only | 0 | 0
raP_Opr_Owner | Sts_OOwned | Output | BOOL |  | 0 | Decimal | 0 | 0 | Status indicating Operator ownership. | Read Only | 0 | 0
raP_Opr_Owner | Sts_POwned | Output | BOOL |  | 0 | Decimal | 0 | 0 | Status indicating Program ownership. | Read Only | 0 | 0
raP_Opr_Owner | Sts_XOwned | Output | BOOL |  | 0 | Decimal | 0 | 0 | Status indicating External ownership. | Read Only | 0 | 0
raP_Opr_Owner | Sts_MOwned | Output | BOOL |  | 0 | Decimal | 0 | 0 | Status indicating Maintenance ownership. | Read Only | 0 | 0
raP_Opr_Owner | Sts_POwnerChanged | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - POwner has changed | Read Only | 0 | 0
raP_Opr_Owner | Sts_XOwnerChanged | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - XOwner has changed | Read Only | 0 | 0
raP_Opr_Owner | Sts_NoCmdSrc | Output | BOOL |  | 0 | Decimal | 0 | 0 | Status indicating the lack of an associated CmdSrc. | Read/Write | 0 | 0
raP_Opr_Owner | Sts_CmdSrcDisabled | Output | BOOL |  | 0 | Decimal | 0 | 0 | Status indicating that the associated CmdSrc is disabled. | Read/Write | 0 | 0
raP_Opr_Owner | Sts_NoArb | Output | BOOL |  | 0 | Decimal | 0 | 0 | Status indicating that there is no ArbitrationQ block associated. | Read/Write | 0 | 0
raP_Opr_Owner | Sts_OUnbound | Output | BOOL | xLax.8 | 0 | Decimal | 0 | 0 | Oper CmdSrc state is not enforced | Read/Write | 0 | 0
raP_Opr_Owner | Sts_PUnbound | Output | BOOL | xLax.9 | 0 | Decimal | 0 | 0 | Prog CmdSrc state is not enforced | Read/Write | 0 | 0
raP_Opr_Owner | Sts_XUnbound | Output | BOOL | xLax.10 | 0 | Decimal | 0 | 0 | Ext CmdSrc state is not enforced | Read/Write | 0 | 0
raP_Opr_Owner | Sts_MUnbound | Output | BOOL | xLax.11 | 0 | Decimal | 0 | 0 | Maint CmdSrc state is not enforced | Read/Write | 0 | 0
raP_Opr_Owner | Val_OOwner | Output | DINT |  | 0 | Decimal | 0 | 0 | ID of the current Operator owner. | Read Only | 0 | 0
raP_Opr_Owner | Val_POwner | Output | DINT |  | 0 | Decimal | 0 | 0 | ID of the current Program owner. | Read Only | 0 | 0
raP_Opr_Owner | Val_XOwner | Output | DINT |  | 0 | Decimal | 0 | 0 | ID of the current External owner. | Read Only | 0 | 0
raP_Opr_Owner | Val_MOwner | Output | DINT |  | 0 | Decimal | 0 | 0 | ID of the current Maintenance owner. | Read/Write | 0 | 0
raP_Opr_Owner | Val_Owner | Output | DINT |  | 0 | Decimal | 0 | 1 | ID of the current dominant owner. | Read Only | 0 | 0
raP_Opr_Prompt | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Opr_Prompt | Out_Cnfrrm | Output | BOOL | Prompt.Out_Cnfrm | 0 | Decimal | 0 | 0 | Operator Confirmation Output. | Read Only | 0 | 0
raP_Opr_Prompt | Out_Rdy | Output | BOOL | Prompt.Out_Rdy | 0 | Decimal | 0 | 0 | 1 = Prompt is Ready to be Displayed. | Read Only | 0 | 0
raP_Opr_Prompt | Out_Select | Output | SINT | Prompt.Out_Select | 4 | Decimal | 0 | 0 | Value of Operator Response to Selector. | Read/Write | 0 | 0
raP_Opr_Prompt | Out_SelectCapt | Output | USINT | Prompt.Out_SelectCapt | 0 | Decimal | 0 | 0 | Captured value of Operator Response to Selector. | Read/Write | 0 | 0
raP_Opr_Prompt | Out_Real0 | Output | REAL | Prompt.Out_Real0 | 0 | Float | 0 | 0 | Real Numeric Value of Operator Entry (0). | Read Only | 0 | 0
raP_Opr_Prompt | Out_Real1 | Output | REAL | Prompt.Out_Real1 | 0 | Float | 0 | 0 | Real Numeric Value of Operator Entry (1). | Read Only | 0 | 0
raP_Opr_Prompt | Out_Real2 | Output | REAL | Prompt.Out_Real2 | 0 | Float | 0 | 0 | Real Numeric Value of Operator Entry (2). | Read Only | 0 | 0
raP_Opr_Prompt | Out_Real3 | Output | REAL | Prompt.Out_Real3 | 0 | Float | 0 | 0 | Real Numeric Value of Operator Entry (3). | Read Only | 0 | 0
raP_Opr_Prompt | Out_Real4 | Output | REAL | Prompt.Out_Real4 | 0 | Float | 0 | 0 | Real Numeric Value of Operator Entry (4) | Read Only | 0 | 0
raP_Opr_Prompt | Out_Real5 | Output | REAL | Prompt.Out_Real5 | 0 | Float | 0 | 0 | Real Numeric Value of Operator Entry (5) | Read Only | 0 | 0
raP_Opr_Prompt | Out_Real6 | Output | REAL | Prompt.Out_Real6 | 0 | Float | 0 | 0 | Real Numeric Value of Operator Entry (6) | Read Only | 0 | 0
raP_Opr_Prompt | Out_Real7 | Output | REAL | Prompt.Out_Real7 | 0 | Float | 0 | 0 | Real Numeric Value of Operator Entry (7) | Read Only | 0 | 0
raP_Opr_Prompt | Val_Ref | Output | DINT | Prompt.Val_Ref | 0 | Decimal | 0 | 0 | Number of Manual Prompt Configuration in the Array Used. | Read Only | 0 | 0
raP_Opr_Prompt | Sts_Alert | Output | BOOL | Prompt.Sts_Alert | 0 | Decimal | 0 | 0 | Status for Alert Breadcrumb. | Read Only | 0 | 0
raP_Opr_Prompt | Sts_AlertTimeOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Alert has timed out. | Read Only | 0 | 0
raP_Opr_Prompt | Sts_RdyCnfrrm | Output | BOOL | Prompt.Sts_RdyCnfrm | 0 | Decimal | 0 | 0 | 1 = The Prompt is ready to be confirmed (completed). | Read Only | 0 | 0
raP_Opr_Prompt | Sts_RdyAck | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = The timeout alarm requires an Acknowledge. | Read Only | 0 | 0
raP_Opr_Prompt | Sts_RdyReset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = The timeout requires a reset. | Read Only | 0 | 0
raP_Opr_Prompt | ORdy_Reset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only | 0 | 0
raP_Opr_Prompt | ORdy_ResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for OCmd_ResetAckAll, enable HMI button. | Read Only | 0 | 0
raP_Opr_Prompt | Sts_RefChg | Output | BOOL | Prompt.Sts_RefChg | 0 | Decimal | 0 | 0 | 1 = The Inp_Ref Has Changed (Single Scan). | Read Only | 0 | 0
raP_Opr_Prompt | Sts_Err | Output | BOOL | Prompt.Sts_Err | 0 | Decimal | 0 | 0 | 1 = Error in Config, see detail bits for reason. | Read Only | 0 | 0
raP_Opr_Prompt | Sts_ErrPromptCfgSize | Output | BOOL | Prompt.Sts_ErrPromptCfgSize | 0 | Decimal | 0 | 0 | 1 = Error in size of an array in the PromptCfg UDT definition. | Read Only | 0 | 0
raP_Opr_Prompt | Sts_ErrRespDataSize | Output | BOOL | Prompt.Sts_ErrRespDataSize | 0 | Decimal | 0 | 0 | 1 = Error in size of an array in the PromptResp UDT definition. | Read Only | 0 | 0
raP_Opr_Prompt | Sts_ErrMsgRef | Output | BOOL | Prompt.Sts_ErrMsgRef | 0 | Decimal | 0 | 0 | 1 = Error in Value of Inp_Ref (past end of prompt array). | Read Only | 0 | 0
raP_Opr_Prompt | Sts_ErrAlm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in Logix tag-based alarm settings. | Read Only | 0 | 0
raP_Opr_Prompt | Sts_Alm | Output | BOOL |  | 0 | Decimal | 0 | 0 | The timeout alarm is active. | Read Only | 0 | 0
raP_Opr_Prompt | Sts_AlmInh | Output | BOOL |  | 0 | Decimal | 0 | 0 | The timeout alarm is inhibited. | Read Only | 0 | 0
raP_Opr_Prompt | Sts_eNotify | Output | DINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read/Write | 0 | 0
raP_Opr_Prompt | Sts_eNotifyAll | Output | DINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values including related objects: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read/Write | 0 | 0
raP_Opr_Prompt | Sts_eNotifyAlertTimeOut | Output | DINT |  | 0 | Decimal | 0 | 0 | AlertTO alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read/Write | 0 | 0
raP_Opr_Prompt | Sts_UnackAlmCount | Output | DINT |  | 0 | Decimal | 0 | 0 | Number of unacknowledged alarms. | Read/Write | 0 | 0
raP_Opr_Prompt | Sts_NRdyCfgErr | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device not ready: configuration error. | Read Only | 0 | 0
raP_Opr_Prompt_Core | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Opr_Prompt_Core | Out_Cnfrm | Output | BOOL |  | 0 | Decimal | 0 | 1 | Operator Confirmation Output. | Read Only | 0 | 0
raP_Opr_Prompt_Core | Out_Rdy | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Prompt is Ready to be Displayed. | Read Only | 0 | 0
raP_Opr_Prompt_Core | Out_Select | Output | SINT | OSet_Select | 4 | Decimal | 0 | 0 | Value of Operator Response to Selector. | Read/Write | 0 | 0
raP_Opr_Prompt_Core | Out_SelectCapt | Output | USINT |  | 0 | Decimal | 0 | 0 | Captured value of Operator Response to Selector. | Read/Write | 0 | 0
raP_Opr_Prompt_Core | Out_Real0 | Output | REAL | Out_Real[0] | 0 | Float | 0 | 0 | Real Numeric Value of Operator Entry (0). | Read Only | 0 | 0
raP_Opr_Prompt_Core | Out_Real1 | Output | REAL | Out_Real[1] | 0 | Float | 0 | 0 | Real Numeric Value of Operator Entry (1). | Read Only | 0 | 0
raP_Opr_Prompt_Core | Out_Real2 | Output | REAL | Out_Real[2] | 0 | Float | 0 | 0 | Real Numeric Value of Operator Entry (2). | Read Only | 0 | 0
raP_Opr_Prompt_Core | Out_Real3 | Output | REAL | Out_Real[3] | 0 | Float | 0 | 0 | Real Numeric Value of Operator Entry (3) | Read Only | 0 | 0
raP_Opr_Prompt_Core | Out_Real4 | Output | REAL | Out_Real[4] | 0 | Float | 0 | 0 | Real Numeric Value of Operator Entry (4) | Read Only | 0 | 0
raP_Opr_Prompt_Core | Out_Real5 | Output | REAL | Out_Real[5] | 0 | Float | 0 | 0 | Real Numeric Value of Operator Entry (5) | Read Only | 0 | 0
raP_Opr_Prompt_Core | Out_Real6 | Output | REAL | Out_Real[6] | 0 | Float | 0 | 0 | Real Numeric Value of Operator Entry (6) | Read Only | 0 | 0
raP_Opr_Prompt_Core | Out_Real7 | Output | REAL | Out_Real[7] | 0 | Float | 0 | 0 | Real Numeric Value of Operator Entry (7) | Read Only | 0 | 0
raP_Opr_Prompt_Core | Val_Ref | Output | DINT |  | 0 | Decimal | 0 | 0 | Number of Manual Prompt Configuration in the Array Used. | Read Only | 0 | 0
raP_Opr_Prompt_Core | Sts_Alert | Output | BOOL |  | 0 | Decimal | 0 | 0 | Status for Alert Breadcrumb. | Read Only | 0 | 0
raP_Opr_Prompt_Core | Sts_RdyCnfrm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = The Prompt is ready to be confirmed (completed). | Read Only | 0 | 0
raP_Opr_Prompt_Core | Sts_RefChg | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = The Inp_Ref Has Changed (Single Scan). | Read Only | 0 | 0
raP_Opr_Prompt_Core | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in Config, see detail bits for reason. | Read Only | 0 | 0
raP_Opr_Prompt_Core | Sts_ErrPromptCfgSize | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in size of an array in the P_PromptCfg UDT definition. | Read Only | 0 | 0
raP_Opr_Prompt_Core | Sts_ErrRespDataSize | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in size of an array in the P_PromptResp UDT definition. | Read Only | 0 | 0
raP_Opr_Prompt_Core | Sts_ErrMsgRef | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in Value of Inp_Ref (past end of prompt array). | Read Only | 0 | 0
raP_Opr_Unit | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Opr_Unit | Out_ExtddAlmsReset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset command to extended alarms. | Read Only | 0 | 0
raP_Opr_Unit | Out_ExtddAlmsResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Reset acknowledge all command to extended alarms. | Read Only | 0 | 0
raP_Opr_Unit | Out_ExtddAlmsDisable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Disable command to extended alarms. | Read Only | 0 | 0
raP_Opr_Unit | Out_ExtddAlmsEnable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Enable command to extended alarms. | Read Only | 0 | 0
raP_Opr_Unit | Out_ExtddAlmsSuppress | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Suppress command to extended alarms. | Read Only | 0 | 0
raP_Opr_Unit | Out_ExtddAlmsUnSuppress | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unsuppress command to extended alarms. | Read Only | 0 | 0
raP_Opr_Unit | Out_ExtddAlmsUnShelve | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unshelve command to extended alarms. | Read Only | 0 | 0
raP_Opr_Unit | Val_Actl | Output | REAL |  | 0 | Float | 0 | 0 | Actual weight/volume/ percent level. | Read Only | 0 | 0
raP_Opr_Unit | Sts_eSummary | Output | INT |  | 0 | Decimal | 0 | 0 | Actualf process summary. | Read Only | 0 | 0
raP_Opr_Unit | Sts | Output | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | Program State Request (bitwise). | Read Only | 0 | 0
raP_Opr_Unit | Sts_Alm | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = An alarm is active. | Read Only | 0 | 0
raP_Opr_Unit | Sts_AlmInh | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is shelved, disabled or suppressed, display icon. | Read Only | 0 | 0
raP_Opr_Unit | Sts_Available | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Available for control by automation (Program). | Read Only | 0 | 0
raP_Opr_Unit | Sts_BypActive | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Bypassing active (Bypassed or Maintenance). | Read Only | 0 | 0
raP_Opr_Unit | Sts_Bypass | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Bypassable interlocks and permissives are bypassed. | Read Only | 0 | 0
raP_Opr_Unit | Sts_MaintByp | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit has a Maintenance bypass function active. | Read Only | 0 | 0
raP_Opr_Unit | Sts_EStop | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Emergency stop ok. | Read Only | 0 | 0
raP_Opr_Unit | Sts_EStopTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit tripped by an EStop not ok. | Read Only | 0 | 0
raP_Opr_Unit | Sts_SStop | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Software stop ok. | Read Only | 0 | 0
raP_Opr_Unit | Sts_SStopTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit tripped by SStop not ok. | Read Only | 0 | 0
raP_Opr_Unit | Sts_eCmd | Output | SINT |  | 0 | Decimal | 0 | 0 | Device Command 0=None 1 = Group Command 1 2 = Group Command 2 3 = Group Command 3 4 = Group Command 4 11 = Source North 12 = Destination North 13 = Source South 14 = Destination South 15 = Source East 16 = Destination East 17 = Source West 18 = Destination West. | Read Only | 0 | 0
raP_Opr_Unit | Sts_eFault | Output | SINT |  | 0 | Decimal | 0 | 0 | Device Fault Status 0 =None, 5 = Device Alarm, 7 = External Alarm, 15 = Interlock trip, 16 = Not ready trip, 34 = Configuration Error. | Read Only | 0 | 0
raP_Opr_Unit | Sts_eFdbk | Output | SINT |  | 0 | Decimal | 0 | 0 | Device Feedback: 0 = Good, 1 = Software Stop, 2 = Emergency stop. | Read Only | 0 | 0
raP_Opr_Unit | Sts_eMtrl | Output | INT |  | 0 | Decimal | 0 | 0 | Actual material type enumeration value. | Read Only | 0 | 0
raP_Opr_Unit | Sts_eState | Output | DINT |  | 0 | Decimal | 0 | 0 | Unit process state. (x) This value represents unit process state (bitwise). | Read Only | 0 | 0
raP_Opr_Unit | Sts_eSts | Output | DINT |  | 0 | Decimal | 0 | 0 | Unit Status: 0 = Powerup / Unknown, 1 = Active, 15 = Out Of service. | Read Only | 0 | 0
raP_Opr_Unit | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Area error. Set if any error is active. See detailed error descriptions for individual reasons. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ErrAlm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in logix tag-based alarm settings. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ErrEU | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Scaled EU Min = Max. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ErrGroupCmd1FailTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Group command 1 fail timer preset: use 0 to 2147483. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ErrGroupCmd2FailTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Group command 2 fail timer preset: use 0 to 2147483. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ErrGroupCmd3FailTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Group command 3 fail timer preset: use 0 to 2147483. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ErrGroupCmd4FailTime | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Group command 4 fail timer preset: use 0 to 2147483. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ErrLimPar | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Scaled EU Min = Max. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ErrPSetPar | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: PSet is invalid. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ErrTypePar | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: No In/Out Parameter Assigned. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ErrLimRpt | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: Scaled EU Min = Max. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ErrPSetRpt | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: PSet is invalid. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ErrTypeRpt | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: No In/Out Parameter Assigned. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ExtddAlms | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An extended alarm is active. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ExtddAlmsAlmInh | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Extended alarm is shelved, disabled or suppressed. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ExtddAlmsAlarmFault | Output | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | Alarm fault extended alarm is present. Each bit represents an individual alarm (0 - 31). | Read Only | 0 | 0
raP_Opr_Unit | Sts_ExtddAlmsDspl | Output | DINT |  | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 0 | 0 | Extended alarm is present for active display (0 - 31). | Read Only | 0 | 0
raP_Opr_Unit | Sts_ExtddAlmsRdyReset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A latched extended alarm is ready to be reset. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ExtddAlmsShelved | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A shelved extended alarm is present. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ExtddAlmsSuppressed | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A suppressed extended alarm is present. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ExtddAlmsDisabled | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A disabled extended alarm is present. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ExtddAlmsUnAckd | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An unacknowledged extended alarm is present. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ExtddAlmMaxCount | Output | SINT |  | 0 | Decimal | 0 | 0 | Indicates the maximum extended alarm active and connected to the object. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ExtddAlmCount | Output | SINT |  | 0 | Decimal | 0 | 0 | Number of extended alarms connected. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ChildrenGood | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = All children are owned and organized. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ChildrenOrganized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = All children are organized. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ChildrenOwned | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = All children are owned. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ChildrenUnBound | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Children ownership unbound. | Read Only | 0 | 0
raP_Opr_Unit | Sts_eNotifyEStopTrip | Output | SINT |  | 0 | Decimal | 0 | 0 | Emergency stop alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Unit | Sts_eNotifySStopTrip | Output | SINT |  | 0 | Decimal | 0 | 0 | Software stop alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Unit | Sts_eNotifyExtddAlms | Output | SINT |  | 0 | Decimal | 0 | 0 | Extended alarms status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Unit | Sts_eNotifyIntlkTrip | Output | SINT |  | 0 | Decimal | 0 | 0 | Interlock Trip alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Unit | Sts_eNotifyGroupCmd1Fail | Output | SINT |  | 0 | Decimal | 0 | 0 | Group command 1 Fail alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Unit | Sts_eNotifyGroupCmd2Fail | Output | SINT |  | 0 | Decimal | 0 | 0 | Group command 2 Fail alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Unit | Sts_eNotifyGroupCmd3Fail | Output | SINT |  | 0 | Decimal | 0 | 0 | Group command 3 Fail alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Unit | Sts_eNotifyGroupCmd4Fail | Output | SINT |  | 0 | Decimal | 0 | 0 | Group command 4 Fail alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Unit | Sts_eNotify | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Unit | Sts_eNotifyAll | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values including related valves: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Unit | Sts_Initialized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Instruction is initialized. Use Inp_InitializeReq to reinitialize. | Read Only | 0 | 0
raP_Opr_Unit | Sts_IntlkTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit tripped by an interlock not ok. | Read Only | 0 | 0
raP_Opr_Unit | Sts_IntlkAvailable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit can be acquired by Program and is available for start/stop control when interlocks are ok. | Read Only | 0 | 0
raP_Opr_Unit | Sts_GroupCmd1Fail | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Group command 1 failed to trip (did not reach state). | Read Only | 0 | 0
raP_Opr_Unit | Sts_GroupCmd2Fail | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Group command 2 failed to trip (did not reach state). | Read Only | 0 | 0
raP_Opr_Unit | Sts_GroupCmd3Fail | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Group command 3 failed to trip (did not reach state). | Read Only | 0 | 0
raP_Opr_Unit | Sts_GroupCmd4Fail | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Group command 4 failed to trip (did not reach state). | Read Only | 0 | 0
raP_Opr_Unit | Sts_MtrlDestinationE | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit to be used as an material destination for a East neighbor connection. | Read Only | 0 | 0
raP_Opr_Unit | Sts_MtrlDestinationN | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit to be used as a material destination for a North neighbor connection. | Read Only | 0 | 0
raP_Opr_Unit | Sts_MtrlDestinationS | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit to be used as a material destination for a South neighbor connection. | Read Only | 0 | 0
raP_Opr_Unit | Sts_MtrlDestinationW | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit to be used as a material destination for a West neighbor connection. | Read Only | 0 | 0
raP_Opr_Unit | Sts_MtrlSourceE | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit to be used as a material source for an East neighbor connection. | Read Only | 0 | 0
raP_Opr_Unit | Sts_MtrlSourceN | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit to be used as a material source for a North neighbor connection. | Read Only | 0 | 0
raP_Opr_Unit | Sts_MtrlSourceS | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit to be used as a material source for a South neighbor connection. | Read Only | 0 | 0
raP_Opr_Unit | Sts_MtrlSourceW | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit to be used as a material source for a West neighbor connection. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ParAdjstd | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Parameter value adjusted. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ParCapture | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Capture Initial parameter setting. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ParClear | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Clear parameter setting. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ParLimFault | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Parameter limit fault. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ParRestore | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Restore initial report setting. | Read Only | 0 | 0
raP_Opr_Unit | Sts_RptAdjstd | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Report value adjusted. | Read Only | 0 | 0
raP_Opr_Unit | Sts_RptCapture | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Capture initial report setting. | Read Only | 0 | 0
raP_Opr_Unit | Sts_RptClear | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Clear report setting. | Read Only | 0 | 0
raP_Opr_Unit | Sts_RptLimFault | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Report limit fault. | Read Only | 0 | 0
raP_Opr_Unit | Sts_RptRestore | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Restore initial report setting. | Read Only | 0 | 0
raP_Opr_Unit | Sts_NotRdy | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Unit is not ready, see detail bits (Sts_Nrdyxxx) for reason. | Read Only | 0 | 0
raP_Opr_Unit | Sts_NrdyChildAlm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit is not ready: child object alarm. | Read Only | 0 | 0
raP_Opr_Unit | Sts_NrdyChildNrdy | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit is not ready: child object not ready. | Read Only | 0 | 0
raP_Opr_Unit | Sts_NrdyExtddAlms | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit is not ready: extended alarms not ok. | Read Only | 0 | 0
raP_Opr_Unit | Sts_NrdyIntlk | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit is not ready: interlock not ok. | Read Only | 0 | 0
raP_Opr_Unit | Sts_NrdyCfgErr | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit is not ready: configuration error. | Read Only | 0 | 0
raP_Opr_Unit | Sts_NrdyOoS | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit is not ready: object disabled by Maintenance. | Read Only | 0 | 0
raP_Opr_Unit | Sts_NrdyPerm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit is not ready: permissive not ok. | Read Only | 0 | 0
raP_Opr_Unit | Sts_NrdySStopTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit is not ready: software stop not ok. | Read Only | 0 | 0
raP_Opr_Unit | Sts_NrdyEStopTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit is not ready: emergency stop not ok. | Read Only | 0 | 0
raP_Opr_Unit | Sts_NrdyChildNotUsable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A child is not usable | Read Only | 0 | 0
raP_Opr_Unit | Sts_NrdyGroupCmd1Perm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit Group command 1 is not ready: permissive not ok. | Read Only | 0 | 0
raP_Opr_Unit | Sts_NrdyGroupCmd2Perm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit Group command 2 is not ready: permissive not ok. | Read Only | 0 | 0
raP_Opr_Unit | Sts_NrdyGroupCmd3Perm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit Group command 3 is not ready: permissive not ok. | Read Only | 0 | 0
raP_Opr_Unit | Sts_NrdyGroupCmd4Perm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Unit Group command 4 is not ready: permissive not ok. | Read Only | 0 | 0
raP_Opr_Unit | Sts_PromptActive | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Prompt Active | Read Only | 0 | 0
raP_Opr_Unit | Sts_Owned | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Child ownership acquired. | Read Only | 0 | 0
raP_Opr_Unit | Sts_RdyAck | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is ready to be acknowledged. | Read Only | 0 | 0
raP_Opr_Unit | Sts_RdyReset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A latched alarm or shed condition is ready to be reset. | Read Only | 0 | 0
raP_Opr_Unit | Sts_RqstdCmd | Output | SINT |  | 2#0000_0000 | Binary | 0 | 0 | Program State Request (bitwise). | Read Only | 0 | 0
raP_Opr_Unit | Sts_Virtual | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = The instruction treats the object as virtual. The instruction acts as normal but the output is kept de-energized (Out_ = 0). 0 = the instruction operates the object normally. | Read Only | 0 | 0
raP_Opr_Unit | Sts_UnackAlmCount | Output | SINT |  | 0 | Decimal | 0 | 0 | Count of unacknowledged alarms. | Read Only | 0 | 0
raP_Opr_Unit | SrcQ_IO | Output | SINT |  | 0 | Decimal | 0 | 0 | Source and quality of primary input or output (enumerated): 0=Good, live, confirmed good 1=Good, live, assumed good 2=Good, no feedback, assumed good 8=Test, virtualized 9=Test, loopback 10=Test, manually entered 16=Uncertain, live, off-spec 17=Uncertain, substituted at device or bus 18=Uncertain, substituted at instruction 19=Uncertain, using last known good 20=Uncertain, using replacement value 32=Bad, signal failure 33=Bad, channel fault 34=Bad, module or communication fault 35=Bad, invalid configuration | Read Only | 0 | 0
raP_Opr_Unit | Sts_eSrc | Output | INT | CmdSrc.Sts_eSrc | 0 | Decimal | 0 | 0 | The current command source enumerated values: 0 = Logic not in use, 4 = Hand, 8 = Maintenance, 16 = Override, 32 = Program, 33 = Program locked, 34 = Program by default (Normal), 64 = Operator, 65 = Operator locked, 66 = Operator by default (Normal), 128 = Maintenance Out of Service, 129 = Programmed Out of Service (rung false), 256 = External. | Read Only | 0 | 0
raP_Opr_Unit | Sts_bSrc | Output | INT | CmdSrc.Sts_bSrc | 0 | Decimal | 0 | 0 | Active selection bitmap (for HMI totem pole with command source request selection): Sts_bSrc.0: hand, Sts_bSrc.1: Programmed Out of service (rung false), Sts_bSrc.2: Maintenance Out of service, Sts_bSrc.3: Maintenance, Sts_bSrc.4: Override, Sts_bSrc.5: External, Sts_bSrc.6: Program locked, Sts_bSrc.7: Program, Sts_bSrc.8: Operator locked, Sts_bSrc.9: Operator. | Read Only | 0 | 0
raP_Opr_Unit | Sts_OoS | Output | BOOL | CmdSrc.Sts_OoS | 0 | Decimal | 0 | 0 | 1 = Out of service is selected (supersedes Maintenance, Override, External, Program, Operator). | Read Only | 0 | 0
raP_Opr_Unit | Sts_Maint | Output | BOOL | CmdSrc.Sts_Maint | 0 | Decimal | 0 | 0 | 1 = Maintenance is selected (supersedes Override, External, Program, Operator). | Read Only | 0 | 0
raP_Opr_Unit | Sts_Ext | Output | BOOL | CmdSrc.Sts_Ext | 0 | Decimal | 0 | 0 | 1 = External is selected (supersedes Program and Operator). | Read Only | 0 | 0
raP_Opr_Unit | Sts_Prog | Output | BOOL | CmdSrc.Sts_Prog | 0 | Decimal | 0 | 0 | 1 = Program is selected. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ProgLocked | Output | BOOL | CmdSrc.Sts_ProgLocked | 0 | Decimal | 0 | 0 | 1 = Program is selected and locked. | Read Only | 0 | 0
raP_Opr_Unit | Sts_Oper | Output | BOOL | CmdSrc.Sts_Oper | 0 | Decimal | 0 | 0 | 1 = Operator is selected. | Read Only | 0 | 0
raP_Opr_Unit | Sts_OperLocked | Output | BOOL | CmdSrc.Sts_OperLocked | 0 | Decimal | 0 | 0 | 1 = Operator is selected and locked. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ProgOperSel | Output | BOOL | CmdSrc.Sts_ProgOperSel | 0 | Decimal | 0 | 0 | Program/Operator selection (latch) state: 1 = Program, 0 = Operator. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ProgOperLock | Output | BOOL | CmdSrc.Sts_ProgOperLock | 0 | Decimal | 0 | 0 | Program/Operator lock (latch) state, 1 = Locked, 0 = Unlocked. | Read Only | 0 | 0
raP_Opr_Unit | Sts_Normal | Output | BOOL | CmdSrc.Sts_Normal | 0 | Decimal | 0 | 0 | 1 = Selection equals the normal (Program or Operator). | Read Only | 0 | 0
raP_Opr_Unit | Sts_ExtReqInh | Output | BOOL | CmdSrc.Sts_ExtReqInh | 0 | Decimal | 0 | 0 | 1 = External request inhibited, cannot get to External from current state. | Read Only | 0 | 0
raP_Opr_Unit | Sts_ProgReqInh | Output | BOOL | CmdSrc.Sts_ProgReqInh | 0 | Decimal | 0 | 0 | 1 = Program request inhibited, cannot get to Program from current state. | Read Only | 0 | 0
raP_Opr_Unit | Sts_MAcqRcvd | Output | BOOL | CmdSrc.Sts_MAcqRcvd | 0 | Decimal | 0 | 0 | 1 = Maintenance acquire command received this scan. | Read Only | 0 | 0
raP_Opr_Unit | Sts_UnqID | Output | DINT |  | 0 | Decimal | 0 | 0 | HMI bus object index. | Read Only | 0 | 0
raP_Opr_Unit | XRdy_Acq | Output | BOOL | CmdSrc.XRdy_Acq | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Acq, enable button. | Read Only | 0 | 0
raP_Opr_Unit | XRdy_Rel | Output | BOOL | CmdSrc.XRdy_Rel | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Rel, enable button. | Read Only | 0 | 0
raP_Opr_Unit | XRdy_OwnerRel | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_OwnerRel, enable button. | Read Only | 0 | 0
raP_Opr_Unit | XRdy_OwnerAcq | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_OwnerAcq, enable HMI button. | Read Only | 0 | 0
raP_Opr_Unit | XRdy | Output | SINT |  | 2#0000_0000 | Binary | 0 | 0 | 1 = Ready for XCmd.(x), enable button. | Read Only | 0 | 0
raP_Opr_Unit | XRdy_Reset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Reset, enable button. | Read Only | 0 | 0
raP_Opr_Unit | XRdy_ResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ResetAckAll, enable button. | Read Only | 0 | 0
raP_Opr_Unit | XRdy_ParCapture | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ParCapture, enable button. | Read Only | 0 | 0
raP_Opr_Unit | XRdy_ParClear | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ParClear, enable button. | Read Only | 0 | 0
raP_Opr_Unit | XRdy_ParRestore | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ParRestore, enable button. | Read Only | 0 | 0
raP_Opr_Unit | XRdy_RptCapture | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_RptCapture, enable button. | Read Only | 0 | 0
raP_Opr_Unit | XRdy_RptClear | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_RptClear, enable button. | Read Only | 0 | 0
raP_Opr_Unit | XRdy_RptRestore | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_RptRestore, enable button. | Read Only | 0 | 0
raP_Tec_HARTChanData_to_PAH | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Tec_HARTChanData_to_PAH | Sts_Initialized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Instruction is initialized. Use Inp_InitializeReq to reinitialize. | Read Only | 0 | 0
raP_Tec_LgxEvent | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Tec_LgxEvent | Sts_Reason | Output | INT |  | 2#0000_0000_0000_0000 | Binary | 0 | 1 | Reason of individual controller event. | Read Only | 0 | 0
raP_Tec_ParRpt | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Tec_ParRpt | Sts_eObjType | Output | SINT |  | 0 | Decimal | 0 | 1 | Object type 0 = ? 1 = Integer 2 = Real, 3 = String, 4 = Enumeration. | Read Only | 0 | 0
raP_Tec_ParRpt | Sts_Adjstd | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Parameter values has been adjusted from initial value (Val_Initial). | Read Only | 0 | 0
raP_Tec_ParRpt | Sts_Capture | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Capture Initial parameter setting. | Read Only | 0 | 0
raP_Tec_ParRpt | Sts_Clear | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Clear parameter setting. | Read Only | 0 | 0
raP_Tec_ParRpt | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: see detail bits for reason. | Read Only | 0 | 0
raP_Tec_ParRpt | Sts_ErrType | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Error in configuration: No In/Out parameter assigned. | Read Only | 0 | 0
raP_Tec_ParRpt | Sts_ErrLim | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Error in configuration: Scaled EU Min = Max. | Read Only | 0 | 0
raP_Tec_ParRpt | Sts_ErrPSet | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 = Error in configuration: PSet is invalid. | Read Only | 0 | 0
raP_Tec_ParRpt | Sts_Initialized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Instruction is initialized. use Inp_InitializeReq to reinitialize. | Read Only | 0 | 0
raP_Tec_ParRpt | Sts_Restore | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Restore initial report setting. | Read Only | 0 | 0
raP_Tec_ParRpt | Val_Initial_E | Output | DINT |  | 0 | Decimal | 0 | 1 | Initial enumeration parameter value, while Inp_Trgr = 1, Val_Initial is set to the parameter setpoint. | Read Only | 0 | 0
raP_Tec_ParRpt | Val_Initial_I | Output | DINT |  | 0 | Decimal | 0 | 1 | Initial integer parameter value, while Inp_Trgr = 1, Val_Initial is set to the parameter setpoint. | Read Only | 0 | 0
raP_Tec_ParRpt | Val_Initial_R | Output | REAL |  | 0 | Float | 0 | 1 | Initial real parameter value, while Inp_Trgr = 1, Val_Initial is set to the parameter setpoint. | Read Only | 0 | 0
raP_Tec_ParRpt | Val_Max_E | Output | DINT |  | 0 | Decimal | 0 | 0 | Maximum enumeration parameter value allowed Val_Max = Cfg_Max OR Val_Max = Val_Initial_E + Cfg_MaxAdjst. | Read Only | 0 | 0
raP_Tec_ParRpt | Val_Min_E | Output | DINT |  | 0 | Decimal | 0 | 0 | Minimum enumeration parameter value allowed Val_Min = Cfg_Min OR Val_Min = Val_Initial_E - Cfg_MinAdjst. | Read Only | 0 | 0
raP_Tec_ParRpt | Val_Max_I | Output | DINT |  | 0 | Decimal | 0 | 0 | Maximum integer parameter value allowed Val_Max = Cfg_Max OR Val_Max = Val_Initial_I + Cfg_MaxAdjst. | Read Only | 0 | 0
raP_Tec_ParRpt | Val_Min_I | Output | DINT |  | 0 | Decimal | 0 | 0 | Minimum integer parameter value allowed Val_Min = Cfg_Min OR Val_Min = Val_Initial_I - Cfg_MinAdjst. | Read Only | 0 | 0
raP_Tec_ParRpt | Val_Max_R | Output | REAL |  | 0 | Float | 0 | 0 | Maximum real parameter value allowed Val_Max = Cfg_Max OR Val_Max = Val_Initial_R + Cfg_MaxAdjst. | Read Only | 0 | 0
raP_Tec_ParRpt | Val_Min_R | Output | REAL |  | 0 | Float | 0 | 0 | Minimum real parameter value allowed Val_Min = Cfg_Min OR Val_Min = Val_Initial_R - Cfg_MinAdjst. | Read Only | 0 | 0
raP_Tec_ParRpt | Val_ParID | Output | SINT |  | 0 | Decimal | 0 | 1 | Parent parameter connection instance ID. Set on scan order. | Read Only | 0 | 0
raP_Tec_ParRpt | Val_RptID | Output | SINT |  | 0 | Decimal | 0 | 1 | Parent report connection instance ID. Set on scan order. | Read Only | 0 | 0
raP_Opr_Seq | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Opr_Seq | Sts_eState | Output | SINT | Wrk_SeqCore.Val_CurrState | 0 | Decimal | 0 | 0 | Numerical value of the current state | Read Only | 0 | 0
raP_Opr_Seq | Val_StepInState | Output | INT | Wrk_SeqCore.Val_StepInState | 0 | Decimal | 0 | 0 | Numerical value of the current state relative step | Read/Write | 0 | 0
raP_Opr_Seq | Val_StepAbs | Output | INT | Wrk_SeqCore.Val_StepAbs | 0 | Decimal | 0 | 1 | Numerical value of the absolute step | Read Only | 0 | 0
raP_Opr_Seq | Val_MaxStepIndex | Output | INT | Wrk_SeqCore.Val_MaxStepIndex | 0 | Decimal | 0 | 0 | Numerical value of the last step array index | Read Only | 0 | 0
raP_Opr_Seq | Val_Qty | Output | INT |  | 0 | Decimal | 0 | 0 | Accepted value of PSet_ / OSet_Qty quantity entry | Read Only | 0 | 0
raP_Opr_Seq | Val_QtyPercent | Output | REAL |  | 0 | Float | 0 | 0 | Quantity As a Percent of Nominal Quantity | Read Only | 0 | 0
raP_Opr_Seq | Val_ScaleFactor | Output | REAL | Wrk_ScaleFactor | 0 | Float | 0 | 0 | Scale Factor where Nominal Quantity = 1.0 | None | 0 | 0
raP_Opr_Seq | Val_Owner | Output | DINT |  | 0 | Decimal | 0 | 0 | Integer owner ID | Read/Write | 0 | 0
raP_Opr_Seq | Out_PromptReq | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Current step is requesting a prompt | Read Only | 0 | 0
raP_Opr_Seq | Out_PromptRef | Output | DINT |  | 0 | Decimal | 0 | 0 | Prompt reference for the currently requested prompt | Read Only | 0 | 0
raP_Opr_Seq | Val_InSeqDays | Output | INT |  | 0 | Decimal | 0 | 0 | Days component since this sequence was started | Read/Write | 0 | 0
raP_Opr_Seq | Val_InSeqHrs | Output | SINT |  | 0 | Decimal | 0 | 0 | Hours component since this sequence was started | Read Only | 0 | 0
raP_Opr_Seq | Val_InSeqMins | Output | SINT |  | 0 | Decimal | 0 | 0 | Minutes component since this sequence was started | Read Only | 0 | 0
raP_Opr_Seq | Val_InSeqSecs | Output | SINT |  | 0 | Decimal | 0 | 0 | Seconds component since this sequence was started | Read Only | 0 | 0
raP_Opr_Seq | Val_InSeqTimeOutPercent | Output | SINT |  | 0 | Decimal | 0 | 0 | Percent of in sequence timeout completed | Read Only | 0 | 0
raP_Opr_Seq | Val_InStateDays | Output | INT |  | 0 | Decimal | 0 | 0 | Days component since this state was started | Read Only | 0 | 0
raP_Opr_Seq | Val_InStateHrs | Output | SINT |  | 0 | Decimal | 0 | 0 | Hours component since this state was started | Read Only | 0 | 0
raP_Opr_Seq | Val_InStateMins | Output | SINT |  | 0 | Decimal | 0 | 0 | Minutes component since this state was started | Read Only | 0 | 0
raP_Opr_Seq | Val_InStateSecs | Output | SINT |  | 0 | Decimal | 0 | 0 | Seconds component since this state was started | Read Only | 0 | 0
raP_Opr_Seq | Val_InStateTimeOutPercent | Output | SINT |  | 0 | Decimal | 0 | 0 | Percent of in state timeout completed | Read Only | 0 | 0
raP_Opr_Seq | Val_InStepDays | Output | INT |  | 0 | Decimal | 0 | 0 | Days component since this step was started | Read Only | 0 | 0
raP_Opr_Seq | Val_InStepHrs | Output | SINT |  | 0 | Decimal | 0 | 0 | Hours compoent since this step was started | Read Only | 0 | 0
raP_Opr_Seq | Val_InStepMins | Output | SINT |  | 0 | Decimal | 0 | 0 | Minutes component since this step was started | Read Only | 0 | 0
raP_Opr_Seq | Val_InStepSecs | Output | SINT |  | 0 | Decimal | 0 | 0 | Seconds component since this step was started | Read Only | 0 | 0
raP_Opr_Seq | Val_InStepTimeOutPercent | Output | SINT |  | 0 | Decimal | 0 | 0 | Percent of in step timeout completed | Read Only | 0 | 0
raP_Opr_Seq | Val_InPauseDays | Output | INT |  | 0 | Decimal | 0 | 0 | Days component since the current pause started | Read/Write | 0 | 0
raP_Opr_Seq | Val_InPauseHrs | Output | SINT |  | 0 | Decimal | 0 | 0 | Hours component since the current pause started | Read Only | 0 | 0
raP_Opr_Seq | Val_InPauseMins | Output | SINT |  | 0 | Decimal | 0 | 0 | Minutes component since the current pause started | Read Only | 0 | 0
raP_Opr_Seq | Val_InPauseSecs | Output | SINT |  | 0 | Decimal | 0 | 0 | Seconds component since the current pause started | Read Only | 0 | 0
raP_Opr_Seq | Val_StepTimerRemainDays | Output | INT |  | 0 | Decimal | 0 | 0 | Days component of the step timer count down | Read Only | 0 | 0
raP_Opr_Seq | Val_StepTimerRemainHrs | Output | SINT |  | 0 | Decimal | 0 | 0 | Hours component of the step timer count down | Read Only | 0 | 0
raP_Opr_Seq | Val_StepTimerRemainMins | Output | SINT |  | 0 | Decimal | 0 | 0 | Minutes component of the step timer count down | Read Only | 0 | 0
raP_Opr_Seq | Val_StepTimerRemainSecs | Output | SINT |  | 0 | Decimal | 0 | 0 | Seconds component of the step timer count down | Read Only | 0 | 0
raP_Opr_Seq | Val_StepTimerRemain | Output | LINT |  | 0 | Decimal | 0 | 0 | Total mSec remaining of the step timer countdown | Read Only | 0 | 0
raP_Opr_Seq | Val_EditStepAbs | Output | DINT | Wrk_SeqEdit.Val_EditStepAbs | 0 | Decimal | 0 | 0 | Absolute Step Number of the edit | Read Only | 0 | 0
raP_Opr_Seq | Val_EditStepNextAbs | Output | DINT | Wrk_SeqEdit.Val_EditStepNextAbs | 0 | Decimal | 0 | 0 | The step following the step to edit | Read Only | 0 | 0
raP_Opr_Seq | Val_EditStepPrevAbs | Output | DINT | Wrk_SeqEdit.Val_EditStepPrevAbs | 0 | Decimal | 0 | 0 | The step before the step to edit | Read Only | 0 | 0
raP_Opr_Seq | Val_NumStepsInEditState | Output | DINT | Wrk_SeqEdit.Val_NumStepsInEditState | 0 | Decimal | 0 | 0 | Number of steps in the edit state | Read Only | 0 | 0
raP_Opr_Seq | Rdy_AddStep | Output | BOOL | Wrk_SeqEdit.Rdy_AddStep | 0 | Decimal | 0 | 0 | 1 - Conditions are appropriate to add a step | Read/Write | 0 | 0
raP_Opr_Seq | Rdy_InsertStep | Output | BOOL | Wrk_SeqEdit.Rdy_InsertStep | 0 | Decimal | 0 | 0 | 1 - Conditions are appropriate to insert a step | Read/Write | 0 | 0
raP_Opr_Seq | Rdy_DeleteStep | Output | BOOL | Wrk_SeqEdit.Rdy_DeleteStep | 0 | Decimal | 0 | 0 | 1 - Conditions are appropriate to delete a step | Read/Write | 0 | 0
raP_Opr_Seq | Rdy_Edit | Output | BOOL | Wrk_SeqEdit.Rdy_Edit | 0 | Decimal | 0 | 0 | 1 - Editing is possible under the current conditions | Read Only | 0 | 0
raP_Opr_Seq | XRdy_Acq | Output | BOOL | CmdSrc.XRdy_Acq | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | XRdy_Rel | Output | BOOL | CmdSrc.XRdy_Rel | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | XRdy_Reset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_Reset, enable button. | Read Only | 0 | 0
raP_Opr_Seq | XRdy_ResetAckAll | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for XCmd_ResetAckAll, enable button | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqIdle | Output | BOOL | StateMachine.bState.0 | 1 | Decimal | 0 | 1 | Idle | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqStarting | Output | BOOL | StateMachine.bState.1 | 0 | Decimal | 0 | 1 | Bit mapped current state | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqRunning | Output | BOOL | StateMachine.bState.2 | 0 | Decimal | 0 | 1 | Running | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqCompleting | Output | BOOL | StateMachine.bState.3 | 0 | Decimal | 0 | 0 | Completing | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqComplete | Output | BOOL | StateMachine.bState.4 | 0 | Decimal | 0 | 1 | Complete | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqSuspending | Output | BOOL | StateMachine.bState.5 | 0 | Decimal | 0 | 0 | Suspending | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqSuspended | Output | BOOL | StateMachine.bState.6 | 0 | Decimal | 0 | 0 | Suspended | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqUnsuspending | Output | BOOL | StateMachine.bState.7 | 0 | Decimal | 0 | 0 | Unsuspending | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqHolding | Output | BOOL | StateMachine.bState.8 | 0 | Decimal | 0 | 1 | Holding | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqHeld | Output | BOOL | StateMachine.bState.9 | 0 | Decimal | 0 | 1 | Held | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqRestarting | Output | BOOL | StateMachine.bState.10 | 0 | Decimal | 0 | 1 | Restarting | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqStopping | Output | BOOL | StateMachine.bState.11 | 0 | Decimal | 0 | 1 | Stopping | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqStopped | Output | BOOL | StateMachine.bState.12 | 0 | Decimal | 0 | 1 | Stopped | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqAborting | Output | BOOL | StateMachine.bState.13 | 0 | Decimal | 0 | 1 | Aborting | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqAborted | Output | BOOL | StateMachine.bState.14 | 0 | Decimal | 0 | 1 | Aborted | Read/Write | 0 | 0
raP_Opr_Seq | Sts_Clearing | Output | BOOL | StateMachine.bState.15 | 0 | Decimal | 0 | 0 | Clearing | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqResetting | Output | BOOL | StateMachine.bState.16 | 0 | Decimal | 0 | 1 | Resetting | Read/Write | 0 | 0
raP_Opr_Seq | Sts_SeqPaused | Output | BOOL | Wrk_SeqCore.Sts_Paused | 0 | Decimal | 0 | 0 | Sequence is paused | Read/Write | 0 | 0
raP_Opr_Seq | Sts_Hand | Output | BOOL | CmdSrc.Sts_Hand | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_OoS | Output | BOOL | CmdSrc.Sts_OoS | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_Maint | Output | BOOL | CmdSrc.Sts_Maint | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_Ovrd | Output | BOOL | CmdSrc.Sts_Ovrd | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_Ext | Output | BOOL | CmdSrc.Sts_Ext | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_Prog | Output | BOOL | CmdSrc.Sts_Prog | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_ProgLocked | Output | BOOL | CmdSrc.Sts_ProgLocked | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_Oper | Output | BOOL | CmdSrc.Sts_Oper | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_OperLocked | Output | BOOL | CmdSrc.Sts_OperLocked | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_ProgOperSel | Output | BOOL | CmdSrc.Sts_ProgOperSel | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_ProgOperLock | Output | BOOL | CmdSrc.Sts_ProgOperLock | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_Normal | Output | BOOL | CmdSrc.Sts_Normal | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_ProgReqInh | Output | BOOL | CmdSrc.Sts_ProgReqInh | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_ExtReqInh | Output | BOOL | CmdSrc.Sts_ExtReqInh | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_MAcqRcvd | Output | BOOL | CmdSrc.Sts_MAcqRcvd | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_bSrc | Output | INT | CmdSrc.Sts_bSrc | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_eSrc | Output | INT | CmdSrc.Sts_eSrc | 0 | Decimal | 0 | 0 | Command Source | Read Only | 0 | 0
raP_Opr_Seq | Sts_StepTimerQualified | Output | BOOL | Wrk_SeqCore.Sts_StepTimerQualified | 0 | Decimal | 0 | 0 | Current step timer is qualified | Read Only | 0 | 0
raP_Opr_Seq | Sts_PromptQualified | Output | BOOL | Wrk_SeqCore.Sts_PromptQualified | 0 | Decimal | 0 | 0 | Current prompt is qualified | Read Only | 0 | 0
raP_Opr_Seq | Sts_Available | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Available for control by automation (Program). | Read Only | 0 | 0
raP_Opr_Seq | Sts_IntlkAvailable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Can be acquired by Program and is available for control when interlocks are OK. | Read Only | 0 | 0
raP_Opr_Seq | Sts_Bypass | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Bypassable interlocks are bypassed. | Read Only | 0 | 0
raP_Opr_Seq | Sts_BypActive | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Interlock bypassing active (bypassed or maintenance). | Read Only | 0 | 0
raP_Opr_Seq | Sts_MaintByp | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device has a maintenance bypass function active. | Read Only | 0 | 0
raP_Opr_Seq | Sts_InStepTimeOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Step has Timed Out | Read Only | 0 | 0
raP_Opr_Seq | Sts_InStateTimeOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = State has Timed Out | Read Only | 0 | 0
raP_Opr_Seq | Sts_InSeqTimeOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Sequence has Timed Out | Read Only | 0 | 0
raP_Opr_Seq | Sts_ErrStepSizeFault | Output | BOOL | Wrk_SeqCore.Sts_ErrStepSize | 0 | Decimal | 0 | 0 | Step array is of an invalid size | Read/Write | 0 | 0
raP_Opr_Seq | Sts_ErrStateSynchFault | Output | BOOL | Wrk_SeqCore.Sts_ErrStateSynch | 0 | Decimal | 0 | 0 | States and Steps are not synchronized | Read Only | 0 | 0
raP_Opr_Seq | Sts_ErrQtyCfg | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in Config: Min, Max, Std Quantity Invalid | Read Only | 0 | 0
raP_Opr_Seq | Sts_ErrQty | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in Config: Entered Quantity Out of Range | Read Only | 0 | 0
raP_Opr_Seq | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in configuration: See detail bits (Sts_Errxxx) for reason. | Read Only | 0 | 0
raP_Opr_Seq | Sts_NrdyOoS | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready: Device disabled by Maintenance. | Read Only | 0 | 0
raP_Opr_Seq | Sts_NrdyPerm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready: Permissive not OK. | Read Only | 0 | 0
raP_Opr_Seq | Sts_NrdyIntlk | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready: Interlock not OK. | Read Only | 0 | 0
raP_Opr_Seq | Sts_NrdyCfgErr | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready: Configuration error. | Read Only | 0 | 0
raP_Opr_Seq | Sts_NrdyChildNotUsable | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A child is not usable | Read Only | 0 | 0
raP_Opr_Seq | Sts_NrdyChildNrdy | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A child is not ready | Read Only | 0 | 0
raP_Opr_Seq | Sts_NotRdy | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready, see detail bits (Sts_Nrdyxxx) for reason. | Read Only | 0 | 0
raP_Opr_Seq | Sts_AlmInh | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is shelved or disabled. | Read Only | 0 | 0
raP_Opr_Seq | Sts_ErrAlm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Error in Logix tag-based alarm settings. | Read Only | 0 | 0
raP_Opr_Seq | Sts_eNotify | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Seq | Sts_eNotifyAll | Output | SINT |  | 0 | Decimal | 0 | 0 | All alarm status enumerated values including related objects: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Seq | Sts_eNotifyIntlkTrip | Output | SINT |  | 0 | Decimal | 0 | 0 | IntlkTrip alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Seq | Sts_eNotifyInSeqTimeOut | Output | SINT |  | 0 | Decimal | 0 | 0 | In Sequence Time Out alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Seq | Sts_eNotifyInStateTimeOut | Output | SINT |  | 0 | Decimal | 0 | 0 | In State Time Out alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Seq | Sts_eNotifyInStepTimeOut | Output | SINT |  | 0 | Decimal | 0 | 0 | In Step Time Out alarm status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. | Read Only | 0 | 0
raP_Opr_Seq | Sts_UnackAlmCount | Output | DINT |  | 0 | Decimal | 0 | 0 | Count of unacknowledged alarms. | Read Only | 0 | 0
raP_Opr_Seq | Sts_RdyAck | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is ready to be acknowledged. | Read Only | 0 | 0
raP_Opr_Seq | Sts_RdyReset | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = A latched alarm or shed condition is ready to be reset. | Read Only | 0 | 0
raP_Opr_Seq | Sts_IntlkTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An Interlock is not OK | Read Only | 0 | 0
raP_Opr_Seq | Sts_Alm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An alarm is active. | Read Only | 0 | 0
raP_Opr_Seq | Sts_ChildrenOwned | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = All children are Owned | Read/Write | 0 | 0
raP_Opr_Seq | Sts_ChildrenOrganized | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = All children are Organized | Read/Write | 0 | 0
raP_Opr_Seq | Sts_ChildrenGood | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = All children are Good | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Out_Qualified | Output | BOOL |  | 0 | Decimal | 0 | 1 | Inputs are in the state required by the step criteria | Read Only | 0 | 0
raP_Opr_SeqBoolInp | Out_BranchQualified | Output | BOOL |  | 0 | Decimal | 0 | 1 | Inputs are in the state required by the step branch criteria | Read Only | 0 | 0
raP_Opr_SeqBoolInp | Sts_MaintByp | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - A Maintenance Bypass is active | Read Only | 0 | 0
raP_Opr_SeqBoolInp | Sts_ErrStepSize | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Step array is an invalid size | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Sts_ErrOutOfRange | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Inp_StepAbs is out of range | Read/Write | 0 | 0
raP_Opr_SeqBoolInp | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - An error is present | Read Only | 0 | 0
raP_Opr_SeqBoolOut | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_0_00 | Output | BOOL | Wrk_bOutputs[0].0 | 0 | Decimal | 0 | 1 | Bank 0 Output 0 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_0_00_EN | Output | BOOL | Wrk_bOutputMask[0].0 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_0_01 | Output | BOOL | Wrk_bOutputs[0].1 | 0 | Decimal | 0 | 1 | Bank 0 Output 1 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_0_01_EN | Output | BOOL | Wrk_bOutputMask[0].1 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_0_02 | Output | BOOL | Wrk_bOutputs[0].2 | 0 | Decimal | 0 | 1 | Bank 0 Output 2 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_0_02_EN | Output | BOOL | Wrk_bOutputMask[0].2 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_0_03 | Output | BOOL | Wrk_bOutputs[0].3 | 0 | Decimal | 0 | 1 | Bank 0 Output 3 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_0_03_EN | Output | BOOL | Wrk_bOutputMask[0].3 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_0_04 | Output | BOOL | Wrk_bOutputs[0].4 | 0 | Decimal | 0 | 1 | Bank 0 Output 4 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_0_04_EN | Output | BOOL | Wrk_bOutputMask[0].4 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_0_05 | Output | BOOL | Wrk_bOutputs[0].5 | 0 | Decimal | 0 | 1 | Bank 0 Output 5 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_0_05_EN | Output | BOOL | Wrk_bOutputMask[0].5 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_0_06 | Output | BOOL | Wrk_bOutputs[0].6 | 0 | Decimal | 0 | 1 | Bank 0 Output 6 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_0_06_EN | Output | BOOL | Wrk_bOutputMask[0].6 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_0_07 | Output | BOOL | Wrk_bOutputs[0].7 | 0 | Decimal | 0 | 1 | Bank 0 Output 7 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_0_07_EN | Output | BOOL | Wrk_bOutputMask[0].7 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_0_08 | Output | BOOL | Wrk_bOutputs[0].8 | 0 | Decimal | 0 | 0 | Bank 0 Output 8 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_0_08_EN | Output | BOOL | Wrk_bOutputMask[0].8 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_0_09 | Output | BOOL | Wrk_bOutputs[0].9 | 0 | Decimal | 0 | 0 | Bank 0 Output 9 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_0_09_EN | Output | BOOL | Wrk_bOutputMask[0].9 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_0_10 | Output | BOOL | Wrk_bOutputs[0].10 | 0 | Decimal | 0 | 0 | Bank 0 Output 10 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_0_10_EN | Output | BOOL | Wrk_bOutputMask[0].10 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_0_11 | Output | BOOL | Wrk_bOutputs[0].11 | 0 | Decimal | 0 | 0 | Bank 0 Output 11 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_0_11_EN | Output | BOOL | Wrk_bOutputMask[0].11 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_0_12 | Output | BOOL | Wrk_bOutputs[0].12 | 0 | Decimal | 0 | 0 | Bank 0 Output 12 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_0_12_EN | Output | BOOL | Wrk_bOutputMask[0].12 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_0_13 | Output | BOOL | Wrk_bOutputs[0].13 | 0 | Decimal | 0 | 0 | Bank 0 Output 13 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_0_13_EN | Output | BOOL | Wrk_bOutputMask[0].13 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_0_14 | Output | BOOL | Wrk_bOutputs[0].14 | 0 | Decimal | 0 | 0 | Bank 0 Output 14 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_0_14_EN | Output | BOOL | Wrk_bOutputMask[0].14 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_0_15 | Output | BOOL | Wrk_bOutputs[0].15 | 0 | Decimal | 0 | 0 | Bank 0 Output 15 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_0_15_EN | Output | BOOL | Wrk_bOutputMask[0].15 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_1_00 | Output | BOOL | Wrk_bOutputs[1].0 | 0 | Decimal | 0 | 0 | Bank 1 Output 0 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_1_00_EN | Output | BOOL | Wrk_bOutputMask[1].0 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_1_01 | Output | BOOL | Wrk_bOutputs[1].1 | 0 | Decimal | 0 | 0 | Bank 1 Output 1 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_1_01_EN | Output | BOOL | Wrk_bOutputMask[1].1 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_1_02 | Output | BOOL | Wrk_bOutputs[1].2 | 0 | Decimal | 0 | 0 | Bank 1 Output 2 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_1_02_EN | Output | BOOL | Wrk_bOutputMask[1].2 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_1_03 | Output | BOOL | Wrk_bOutputs[1].3 | 0 | Decimal | 0 | 0 | Bank 1 Output 3 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_1_03_EN | Output | BOOL | Wrk_bOutputMask[1].3 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_1_04 | Output | BOOL | Wrk_bOutputs[1].4 | 0 | Decimal | 0 | 0 | Bank 1 Output 4 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_1_04_EN | Output | BOOL | Wrk_bOutputMask[1].4 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_1_05 | Output | BOOL | Wrk_bOutputs[1].5 | 0 | Decimal | 0 | 0 | Bank 1 Output 5 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_1_05_EN | Output | BOOL | Wrk_bOutputMask[1].5 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_1_06 | Output | BOOL | Wrk_bOutputs[1].6 | 0 | Decimal | 0 | 0 | Bank 1 Output 6 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_1_06_EN | Output | BOOL | Wrk_bOutputMask[1].6 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_1_07 | Output | BOOL | Wrk_bOutputs[1].7 | 0 | Decimal | 0 | 0 | Bank 1 Output 7 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_1_07_EN | Output | BOOL | Wrk_bOutputMask[1].7 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_1_08 | Output | BOOL | Wrk_bOutputs[1].8 | 0 | Decimal | 0 | 0 | Bank 1 Output 8 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_1_08_EN | Output | BOOL | Wrk_bOutputMask[1].8 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_1_09 | Output | BOOL | Wrk_bOutputs[1].9 | 0 | Decimal | 0 | 0 | Bank 1 Output 9 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_1_09_EN | Output | BOOL | Wrk_bOutputMask[1].9 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_1_10 | Output | BOOL | Wrk_bOutputs[1].10 | 0 | Decimal | 0 | 0 | Bank 1 Output 10 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_1_10_EN | Output | BOOL | Wrk_bOutputMask[1].10 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_1_11 | Output | BOOL | Wrk_bOutputs[1].11 | 0 | Decimal | 0 | 0 | Bank 1 Output 11 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_1_11_EN | Output | BOOL | Wrk_bOutputMask[1].11 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_1_12 | Output | BOOL | Wrk_bOutputs[1].12 | 0 | Decimal | 0 | 0 | Bank 1 Output 12 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_1_12_EN | Output | BOOL | Wrk_bOutputMask[1].12 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_1_13 | Output | BOOL | Wrk_bOutputs[1].13 | 0 | Decimal | 0 | 0 | Bank 1 Output 13 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_1_13_EN | Output | BOOL | Wrk_bOutputMask[1].13 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_1_14 | Output | BOOL | Wrk_bOutputs[1].14 | 0 | Decimal | 0 | 0 | Bank 1 Output 14 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_1_14_EN | Output | BOOL | Wrk_bOutputMask[1].14 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_1_15 | Output | BOOL | Wrk_bOutputs[1].15 | 0 | Decimal | 0 | 0 | Bank 1 Output 15 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_1_15_EN | Output | BOOL | Wrk_bOutputMask[1].15 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_2_00 | Output | BOOL | Wrk_bOutputs[2].00 | 0 | Decimal | 0 | 0 | Bank 2 Output 0 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_2_00_EN | Output | BOOL | Wrk_bOutputMask[2].0 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_2_01 | Output | BOOL | Wrk_bOutputs[2].01 | 0 | Decimal | 0 | 0 | Bank 2 Output 1 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_2_01_EN | Output | BOOL | Wrk_bOutputMask[2].1 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_2_02 | Output | BOOL | Wrk_bOutputs[2].02 | 0 | Decimal | 0 | 0 | Bank 2 Output 2 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_2_02_EN | Output | BOOL | Wrk_bOutputMask[2].2 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_2_03 | Output | BOOL | Wrk_bOutputs[2].03 | 0 | Decimal | 0 | 0 | Bank 2 Output 3 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_2_03_EN | Output | BOOL | Wrk_bOutputMask[2].3 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_2_04 | Output | BOOL | Wrk_bOutputs[2].04 | 0 | Decimal | 0 | 0 | Bank 2 Output 4 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_2_04_EN | Output | BOOL | Wrk_bOutputMask[2].4 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_2_05 | Output | BOOL | Wrk_bOutputs[2].05 | 0 | Decimal | 0 | 0 | Bank 2 Output 5 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_2_05_EN | Output | BOOL | Wrk_bOutputMask[2].5 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_2_06 | Output | BOOL | Wrk_bOutputs[2].06 | 0 | Decimal | 0 | 0 | Bank 2 Output 6 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_2_06_EN | Output | BOOL | Wrk_bOutputMask[2].6 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_2_07 | Output | BOOL | Wrk_bOutputs[2].07 | 0 | Decimal | 0 | 0 | Bank 2 Output 7 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_2_07_EN | Output | BOOL | Wrk_bOutputMask[2].7 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_2_08 | Output | BOOL | Wrk_bOutputs[2].08 | 0 | Decimal | 0 | 0 | Bank 2 Output 8 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_2_08_EN | Output | BOOL | Wrk_bOutputMask[2].8 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_2_09 | Output | BOOL | Wrk_bOutputs[2].09 | 0 | Decimal | 0 | 0 | Bank 2 Output 9 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_2_09_EN | Output | BOOL | Wrk_bOutputMask[2].9 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_2_10 | Output | BOOL | Wrk_bOutputs[2].10 | 0 | Decimal | 0 | 0 | Bank 2 Output 10 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_2_10_EN | Output | BOOL | Wrk_bOutputMask[2].10 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_2_11 | Output | BOOL | Wrk_bOutputs[2].11 | 0 | Decimal | 0 | 0 | Bank 2 Output 11 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_2_11_EN | Output | BOOL | Wrk_bOutputMask[2].11 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_2_12 | Output | BOOL | Wrk_bOutputs[2].12 | 0 | Decimal | 0 | 0 | Bank 2 Output 12 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_2_12_EN | Output | BOOL | Wrk_bOutputMask[2].12 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_2_13 | Output | BOOL | Wrk_bOutputs[2].13 | 0 | Decimal | 0 | 0 | Bank 2 Output 13 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_2_13_EN | Output | BOOL | Wrk_bOutputMask[2].13 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_2_14 | Output | BOOL | Wrk_bOutputs[2].14 | 0 | Decimal | 0 | 0 | Bank 2 Output 14 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_2_14_EN | Output | BOOL | Wrk_bOutputMask[2].14 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_2_15 | Output | BOOL | Wrk_bOutputs[2].15 | 0 | Decimal | 0 | 0 | Bank 2 Output 15 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_2_15_EN | Output | BOOL | Wrk_bOutputMask[2].15 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_3_00 | Output | BOOL | Wrk_bOutputs[3].00 | 0 | Decimal | 0 | 0 | Bank 3 Output 0 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_3_00_EN | Output | BOOL | Wrk_bOutputMask[3].00 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_3_01 | Output | BOOL | Wrk_bOutputs[3].01 | 0 | Decimal | 0 | 0 | Bank 3 Output 1 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_3_01_EN | Output | BOOL | Wrk_bOutputMask[3].01 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_3_02 | Output | BOOL | Wrk_bOutputs[3].02 | 0 | Decimal | 0 | 0 | Bank 3 Output 2 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_3_02_EN | Output | BOOL | Wrk_bOutputMask[3].02 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_3_03 | Output | BOOL | Wrk_bOutputs[3].03 | 0 | Decimal | 0 | 0 | Bank 3 Output 3 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_3_03_EN | Output | BOOL | Wrk_bOutputMask[3].03 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_3_04 | Output | BOOL | Wrk_bOutputs[3].04 | 0 | Decimal | 0 | 0 | Bank 3 Output 4 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_3_04_EN | Output | BOOL | Wrk_bOutputMask[3].04 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_3_05 | Output | BOOL | Wrk_bOutputs[3].05 | 0 | Decimal | 0 | 0 | Bank 3 Output 5 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_3_05_EN | Output | BOOL | Wrk_bOutputMask[3].05 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_3_06 | Output | BOOL | Wrk_bOutputs[3].06 | 0 | Decimal | 0 | 0 | Bank 3 Output 6 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_3_06_EN | Output | BOOL | Wrk_bOutputMask[3].06 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_3_07 | Output | BOOL | Wrk_bOutputs[3].07 | 0 | Decimal | 0 | 0 | Bank 3 Output 7 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_3_07_EN | Output | BOOL | Wrk_bOutputMask[3].07 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_3_08 | Output | BOOL | Wrk_bOutputs[3].08 | 0 | Decimal | 0 | 0 | Bank 3 Output 8 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_3_08_EN | Output | BOOL | Wrk_bOutputMask[3].08 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_3_09 | Output | BOOL | Wrk_bOutputs[3].09 | 0 | Decimal | 0 | 0 | Bank 3 Output 9 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_3_09_EN | Output | BOOL | Wrk_bOutputMask[3].09 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_3_10 | Output | BOOL | Wrk_bOutputs[3].10 | 0 | Decimal | 0 | 0 | Bank 3 Output 10 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_3_10_EN | Output | BOOL | Wrk_bOutputMask[3].10 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_3_11 | Output | BOOL | Wrk_bOutputs[3].11 | 0 | Decimal | 0 | 0 | Bank 3 Output 11 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_3_11_EN | Output | BOOL | Wrk_bOutputMask[3].11 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_3_12 | Output | BOOL | Wrk_bOutputs[3].12 | 0 | Decimal | 0 | 0 | Bank 3 Output 12 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_3_12_EN | Output | BOOL | Wrk_bOutputMask[3].12 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_3_13 | Output | BOOL | Wrk_bOutputs[3].13 | 0 | Decimal | 0 | 0 | Bank 3 Output 13 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_3_13_EN | Output | BOOL | Wrk_bOutputMask[3].13 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_3_14 | Output | BOOL | Wrk_bOutputs[3].14 | 0 | Decimal | 0 | 0 | Bank 3 Output 14 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_3_14_EN | Output | BOOL | Wrk_bOutputMask[3].14 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_3_15 | Output | BOOL | Wrk_bOutputs[3].15 | 0 | Decimal | 0 | 0 | Bank 3 Output 15 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_3_15_EN | Output | BOOL | Wrk_bOutputMask[3].15 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_4_00 | Output | BOOL | Wrk_bOutputs[4].00 | 0 | Decimal | 0 | 0 | Bank 4 Output 0 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_4_00_EN | Output | BOOL | Wrk_bOutputMask[4].00 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_4_01 | Output | BOOL | Wrk_bOutputs[4].01 | 0 | Decimal | 0 | 0 | Bank 4 Output 1 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_4_01_EN | Output | BOOL | Wrk_bOutputMask[4].01 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_4_02 | Output | BOOL | Wrk_bOutputs[4].02 | 0 | Decimal | 0 | 0 | Bank 4 Output 2 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_4_02_EN | Output | BOOL | Wrk_bOutputMask[4].02 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_4_03 | Output | BOOL | Wrk_bOutputs[4].03 | 0 | Decimal | 0 | 0 | Bank 4 Output 3 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_4_03_EN | Output | BOOL | Wrk_bOutputMask[4].03 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_4_04 | Output | BOOL | Wrk_bOutputs[4].04 | 0 | Decimal | 0 | 0 | Bank 4 Output 4 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_4_04_EN | Output | BOOL | Wrk_bOutputMask[4].04 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_4_05 | Output | BOOL | Wrk_bOutputs[4].05 | 0 | Decimal | 0 | 0 | Bank 4 Output 5 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_4_05_EN | Output | BOOL | Wrk_bOutputMask[4].05 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_4_06 | Output | BOOL | Wrk_bOutputs[4].06 | 0 | Decimal | 0 | 0 | Bank 4 Output 6 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_4_06_EN | Output | BOOL | Wrk_bOutputMask[4].06 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_4_07 | Output | BOOL | Wrk_bOutputs[4].07 | 0 | Decimal | 0 | 0 | Bank 4 Output 7 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_4_07_EN | Output | BOOL | Wrk_bOutputMask[4].07 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_4_08 | Output | BOOL | Wrk_bOutputs[4].08 | 0 | Decimal | 0 | 0 | Bank 4 Output 8 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_4_08_EN | Output | BOOL | Wrk_bOutputMask[4].08 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_4_09 | Output | BOOL | Wrk_bOutputs[4].09 | 0 | Decimal | 0 | 0 | Bank 4 Output 9 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_4_09_EN | Output | BOOL | Wrk_bOutputMask[4].09 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_4_10 | Output | BOOL | Wrk_bOutputs[4].10 | 0 | Decimal | 0 | 0 | Bank 4 Output 10 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_4_10_EN | Output | BOOL | Wrk_bOutputMask[4].10 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_4_11 | Output | BOOL | Wrk_bOutputs[4].11 | 0 | Decimal | 0 | 0 | Bank 4 Output 11 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_4_11_EN | Output | BOOL | Wrk_bOutputMask[4].11 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_4_12 | Output | BOOL | Wrk_bOutputs[4].12 | 0 | Decimal | 0 | 0 | Bank 4 Output 12 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_4_12_EN | Output | BOOL | Wrk_bOutputMask[4].12 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_4_13 | Output | BOOL | Wrk_bOutputs[4].13 | 0 | Decimal | 0 | 0 | Bank 4 Output 13 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_4_13_EN | Output | BOOL | Wrk_bOutputMask[4].13 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_4_14 | Output | BOOL | Wrk_bOutputs[4].14 | 0 | Decimal | 0 | 0 | Bank 4 Output 14 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_4_14_EN | Output | BOOL | Wrk_bOutputMask[4].14 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_4_15 | Output | BOOL | Wrk_bOutputs[4].15 | 0 | Decimal | 0 | 0 | Bank 4 Output 15 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_4_15_EN | Output | BOOL | Wrk_bOutputMask[4].15 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_5_00 | Output | BOOL | Wrk_bOutputs[5].00 | 0 | Decimal | 0 | 0 | Bank 5 Output 0 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_5_00_EN | Output | BOOL | Wrk_bOutputMask[5].0 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_5_01 | Output | BOOL | Wrk_bOutputs[5].01 | 0 | Decimal | 0 | 0 | Bank 5 Output 1 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_5_01_EN | Output | BOOL | Wrk_bOutputMask[5].1 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_5_02 | Output | BOOL | Wrk_bOutputs[5].02 | 0 | Decimal | 0 | 0 | Bank 5 Output 2 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_5_02_EN | Output | BOOL | Wrk_bOutputMask[5].2 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_5_03 | Output | BOOL | Wrk_bOutputs[5].03 | 0 | Decimal | 0 | 0 | Bank 5 Output 3 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_5_03_EN | Output | BOOL | Wrk_bOutputMask[5].3 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_5_04 | Output | BOOL | Wrk_bOutputs[5].04 | 0 | Decimal | 0 | 0 | Bank 5 Output 4 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_5_04_EN | Output | BOOL | Wrk_bOutputMask[5].4 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_5_05 | Output | BOOL | Wrk_bOutputs[5].05 | 0 | Decimal | 0 | 0 | Bank 5 Output 5 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_5_05_EN | Output | BOOL | Wrk_bOutputMask[5].5 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_5_06 | Output | BOOL | Wrk_bOutputs[5].06 | 0 | Decimal | 0 | 0 | Bank 5 Output 6 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_5_06_EN | Output | BOOL | Wrk_bOutputMask[5].6 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_5_07 | Output | BOOL | Wrk_bOutputs[5].07 | 0 | Decimal | 0 | 0 | Bank 5 Output 7 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_5_07_EN | Output | BOOL | Wrk_bOutputMask[5].7 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_5_08 | Output | BOOL | Wrk_bOutputs[5].08 | 0 | Decimal | 0 | 0 | Bank 5 Output 8 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_5_08_EN | Output | BOOL | Wrk_bOutputMask[5].8 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_5_09 | Output | BOOL | Wrk_bOutputs[5].09 | 0 | Decimal | 0 | 0 | Bank 5 Output 9 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_5_09_EN | Output | BOOL | Wrk_bOutputMask[5].9 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_5_10 | Output | BOOL | Wrk_bOutputs[5].10 | 0 | Decimal | 0 | 0 | Bank 5 Output 10 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_5_10_EN | Output | BOOL | Wrk_bOutputMask[5].10 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_5_11 | Output | BOOL | Wrk_bOutputs[5].11 | 0 | Decimal | 0 | 0 | Bank 5 Output 11 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_5_11_EN | Output | BOOL | Wrk_bOutputMask[5].11 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_5_12 | Output | BOOL | Wrk_bOutputs[5].12 | 0 | Decimal | 0 | 0 | Bank 5 Output 12 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_5_12_EN | Output | BOOL | Wrk_bOutputMask[5].12 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_5_13 | Output | BOOL | Wrk_bOutputs[5].13 | 0 | Decimal | 0 | 0 | Bank 5 Output 13 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_5_13_EN | Output | BOOL | Wrk_bOutputMask[5].13 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_5_14 | Output | BOOL | Wrk_bOutputs[5].14 | 0 | Decimal | 0 | 0 | Bank 5 Output 14 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_5_14_EN | Output | BOOL | Wrk_bOutputMask[5].14 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_5_15 | Output | BOOL | Wrk_bOutputs[5].15 | 0 | Decimal | 0 | 0 | Bank 5 Output 15 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_5_15_EN | Output | BOOL | Wrk_bOutputMask[5].15 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_6_00 | Output | BOOL | Wrk_bOutputs[6].00 | 0 | Decimal | 0 | 0 | Bank 6 Output 0 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_6_00_EN | Output | BOOL | Wrk_bOutputMask[6].00 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_6_01 | Output | BOOL | Wrk_bOutputs[6].01 | 0 | Decimal | 0 | 0 | Bank 6 Output 1 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_6_01_EN | Output | BOOL | Wrk_bOutputMask[6].01 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_6_02 | Output | BOOL | Wrk_bOutputs[6].02 | 0 | Decimal | 0 | 0 | Bank 6 Output 2 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_6_02_EN | Output | BOOL | Wrk_bOutputMask[6].02 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_6_03 | Output | BOOL | Wrk_bOutputs[6].03 | 0 | Decimal | 0 | 0 | Bank 6 Output 3 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_6_03_EN | Output | BOOL | Wrk_bOutputMask[6].03 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_6_04 | Output | BOOL | Wrk_bOutputs[6].04 | 0 | Decimal | 0 | 0 | Bank 6 Output 4 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_6_04_EN | Output | BOOL | Wrk_bOutputMask[6].04 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_6_05 | Output | BOOL | Wrk_bOutputs[6].05 | 0 | Decimal | 0 | 0 | Bank 6 Output 5 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_6_05_EN | Output | BOOL | Wrk_bOutputMask[6].05 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_6_06 | Output | BOOL | Wrk_bOutputs[6].06 | 0 | Decimal | 0 | 0 | Bank 6 Output 6 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_6_06_EN | Output | BOOL | Wrk_bOutputMask[6].06 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_6_07 | Output | BOOL | Wrk_bOutputs[6].07 | 0 | Decimal | 0 | 0 | Bank 6 Output 7 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_6_07_EN | Output | BOOL | Wrk_bOutputMask[6].07 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_6_08 | Output | BOOL | Wrk_bOutputs[6].08 | 0 | Decimal | 0 | 0 | Bank 6 Output 8 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_6_08_EN | Output | BOOL | Wrk_bOutputMask[6].08 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_6_09 | Output | BOOL | Wrk_bOutputs[6].09 | 0 | Decimal | 0 | 0 | Bank 6 Output 9 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_6_09_EN | Output | BOOL | Wrk_bOutputMask[6].09 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_6_10 | Output | BOOL | Wrk_bOutputs[6].10 | 0 | Decimal | 0 | 0 | Bank 6 Output 10 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_6_10_EN | Output | BOOL | Wrk_bOutputMask[6].10 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_6_11 | Output | BOOL | Wrk_bOutputs[6].11 | 0 | Decimal | 0 | 0 | Bank 6 Output 11 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_6_11_EN | Output | BOOL | Wrk_bOutputMask[6].11 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_6_12 | Output | BOOL | Wrk_bOutputs[6].12 | 0 | Decimal | 0 | 0 | Bank 6 Output 12 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_6_12_EN | Output | BOOL | Wrk_bOutputMask[6].12 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_6_13 | Output | BOOL | Wrk_bOutputs[6].13 | 0 | Decimal | 0 | 0 | Bank 6 Output 13 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_6_13_EN | Output | BOOL | Wrk_bOutputMask[6].13 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_6_14 | Output | BOOL | Wrk_bOutputs[6].14 | 0 | Decimal | 0 | 0 | Bank 6 Output 14 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_6_14_EN | Output | BOOL | Wrk_bOutputMask[6].14 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_6_15 | Output | BOOL | Wrk_bOutputs[6].15 | 0 | Decimal | 0 | 0 | Bank 6 Output 15 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_6_15_EN | Output | BOOL | Wrk_bOutputMask[6].15 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_7_00 | Output | BOOL | Wrk_bOutputs[7].00 | 0 | Decimal | 0 | 0 | Bank 7 Output 0 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_7_00_EN | Output | BOOL | Wrk_bOutputMask[7].00 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_7_01 | Output | BOOL | Wrk_bOutputs[7].01 | 0 | Decimal | 0 | 0 | Bank 7 Output 1 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_7_01_EN | Output | BOOL | Wrk_bOutputMask[7].01 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_7_02 | Output | BOOL | Wrk_bOutputs[7].02 | 0 | Decimal | 0 | 0 | Bank 7 Output 2 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_7_02_EN | Output | BOOL | Wrk_bOutputMask[7].02 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_7_03 | Output | BOOL | Wrk_bOutputs[7].03 | 0 | Decimal | 0 | 0 | Bank 7 Output 3 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_7_03_EN | Output | BOOL | Wrk_bOutputMask[7].03 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_7_04 | Output | BOOL | Wrk_bOutputs[7].04 | 0 | Decimal | 0 | 0 | Bank 7 Output 4 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_7_04_EN | Output | BOOL | Wrk_bOutputMask[7].04 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_7_05 | Output | BOOL | Wrk_bOutputs[7].05 | 0 | Decimal | 0 | 0 | Bank 7 Output 5 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_7_05_EN | Output | BOOL | Wrk_bOutputMask[7].05 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_7_06 | Output | BOOL | Wrk_bOutputs[7].06 | 0 | Decimal | 0 | 0 | Bank 7 Output 6 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_7_06_EN | Output | BOOL | Wrk_bOutputMask[7].06 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_7_07 | Output | BOOL | Wrk_bOutputs[7].07 | 0 | Decimal | 0 | 0 | Bank 7 Output 7 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_7_07_EN | Output | BOOL | Wrk_bOutputMask[7].07 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_7_08 | Output | BOOL | Wrk_bOutputs[7].08 | 0 | Decimal | 0 | 0 | Bank 7 Output 8 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_7_08_EN | Output | BOOL | Wrk_bOutputMask[7].08 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_7_09 | Output | BOOL | Wrk_bOutputs[7].09 | 0 | Decimal | 0 | 0 | Bank 7 Output 9 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_7_09_EN | Output | BOOL | Wrk_bOutputMask[7].09 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_7_10 | Output | BOOL | Wrk_bOutputs[7].10 | 0 | Decimal | 0 | 0 | Bank 7 Output 10 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_7_10_EN | Output | BOOL | Wrk_bOutputMask[7].10 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_7_11 | Output | BOOL | Wrk_bOutputs[7].11 | 0 | Decimal | 0 | 0 | Bank 7 Output 11 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_7_11_EN | Output | BOOL | Wrk_bOutputMask[7].11 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_7_12 | Output | BOOL | Wrk_bOutputs[7].12 | 0 | Decimal | 0 | 0 | Bank 7 Output 12 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_7_12_EN | Output | BOOL | Wrk_bOutputMask[7].12 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_7_13 | Output | BOOL | Wrk_bOutputs[7].13 | 0 | Decimal | 0 | 0 | Bank 7 Output 13 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_7_13_EN | Output | BOOL | Wrk_bOutputMask[7].13 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_7_14 | Output | BOOL | Wrk_bOutputs[7].14 | 0 | Decimal | 0 | 0 | Bank 7 Output 14 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_7_14_EN | Output | BOOL | Wrk_bOutputMask[7].14 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Out_7_15 | Output | BOOL | Wrk_bOutputs[7].15 | 0 | Decimal | 0 | 0 | Bank 7 Output 15 | Read/Write | 0 | 0
raP_Opr_SeqBoolOut | Out_7_15_EN | Output | BOOL | Wrk_bOutputMask[7].15 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Sts_ErrStepSize | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Step array is an invalid size | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Sts_ErrOutOfRange | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Inp_StepAbs is out of range | Read Only | 0 | 0
raP_Opr_SeqBoolOut | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 - An error is present | Read Only | 0 | 0
raP_Opr_SeqRealOut | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_0_00 | Output | REAL | Wrk_Outputs[0] | 0 | Float | 0 | 1 | Bank 0 Output 0 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_0_00_EN | Output | BOOL | Wrk_bOutputMask[0].0 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_0_01 | Output | REAL | Wrk_Outputs[1] | 0 | Float | 0 | 1 | Bank 0 Output 1 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_0_01_EN | Output | BOOL | Wrk_bOutputMask[0].1 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_0_02 | Output | REAL | Wrk_Outputs[2] | 0 | Float | 0 | 1 | Bank 0 Output 2 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_0_02_EN | Output | BOOL | Wrk_bOutputMask[0].2 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_0_03 | Output | REAL | Wrk_Outputs[3] | 0 | Float | 0 | 1 | Bank 0 Output 3 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_0_03_EN | Output | BOOL | Wrk_bOutputMask[0].3 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_0_04 | Output | REAL | Wrk_Outputs[4] | 0 | Float | 0 | 1 | Bank 0 Output 4 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_0_04_EN | Output | BOOL | Wrk_bOutputMask[0].4 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_0_05 | Output | REAL | Wrk_Outputs[5] | 0 | Float | 0 | 1 | Bank 0 Output 5 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_0_05_EN | Output | BOOL | Wrk_bOutputMask[0].5 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_0_06 | Output | REAL | Wrk_Outputs[6] | 0 | Float | 0 | 1 | Bank 0 Output 6 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_0_06_EN | Output | BOOL | Wrk_bOutputMask[0].6 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_0_07 | Output | REAL | Wrk_Outputs[7] | 0 | Float | 0 | 1 | Bank 0 Output 7 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_0_07_EN | Output | BOOL | Wrk_bOutputMask[0].7 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_1_00 | Output | REAL | Wrk_Outputs[8] | 0 | Float | 0 | 0 | Bank 1 Output 0 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_1_00_EN | Output | BOOL | Wrk_bOutputMask[1].0 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_1_01 | Output | REAL | Wrk_Outputs[9] | 0 | Float | 0 | 0 | Bank 1 Output 1 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_1_01_EN | Output | BOOL | Wrk_bOutputMask[1].1 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_1_02 | Output | REAL | Wrk_Outputs[10] | 0 | Float | 0 | 0 | Bank 1 Output 2 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_1_02_EN | Output | BOOL | Wrk_bOutputMask[1].2 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_1_03 | Output | REAL | Wrk_Outputs[11] | 0 | Float | 0 | 0 | Bank 1 Output 3 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_1_03_EN | Output | BOOL | Wrk_bOutputMask[1].3 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_1_04 | Output | REAL | Wrk_Outputs[12] | 0 | Float | 0 | 0 | Bank 1 Output 4 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_1_04_EN | Output | BOOL | Wrk_bOutputMask[1].4 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_1_05 | Output | REAL | Wrk_Outputs[13] | 0 | Float | 0 | 0 | Bank 1 Output 5 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_1_05_EN | Output | BOOL | Wrk_bOutputMask[1].5 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_1_06 | Output | REAL | Wrk_Outputs[14] | 0 | Float | 0 | 0 | Bank 1 Output 6 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_1_06_EN | Output | BOOL | Wrk_bOutputMask[1].6 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_1_07 | Output | REAL | Wrk_Outputs[15] | 0 | Float | 0 | 0 | Bank 1 Output 7 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_1_07_EN | Output | BOOL | Wrk_bOutputMask[1].7 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_2_00 | Output | REAL | Wrk_Outputs[16] | 0 | Float | 0 | 0 | Bank 2 Output 0 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_2_00_EN | Output | BOOL | Wrk_bOutputMask[2].0 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_2_01 | Output | REAL | Wrk_Outputs[17] | 0 | Float | 0 | 0 | Bank 2 Output 1 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_2_01_EN | Output | BOOL | Wrk_bOutputMask[2].1 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_2_02 | Output | REAL | Wrk_Outputs[18] | 0 | Float | 0 | 0 | Bank 2 Output 2 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_2_02_EN | Output | BOOL | Wrk_bOutputMask[2].2 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_2_03 | Output | REAL | Wrk_Outputs[19] | 0 | Float | 0 | 0 | Bank 2 Output 3 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_2_03_EN | Output | BOOL | Wrk_bOutputMask[2].3 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_2_04 | Output | REAL | Wrk_Outputs[20] | 0 | Float | 0 | 0 | Bank 2 Output 4 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_2_04_EN | Output | BOOL | Wrk_bOutputMask[2].4 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_2_05 | Output | REAL | Wrk_Outputs[21] | 0 | Float | 0 | 0 | Bank 2 Output 5 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_2_05_EN | Output | BOOL | Wrk_bOutputMask[2].5 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_2_06 | Output | REAL | Wrk_Outputs[22] | 0 | Float | 0 | 0 | Bank 2 Output 6 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_2_06_EN | Output | BOOL | Wrk_bOutputMask[2].6 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_2_07 | Output | REAL | Wrk_Outputs[23] | 0 | Float | 0 | 0 | Bank 2 Output 7 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_2_07_EN | Output | BOOL | Wrk_bOutputMask[2].7 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_3_00 | Output | REAL | Wrk_Outputs[24] | 0 | Float | 0 | 0 | Bank 3 Output 0 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_3_00_EN | Output | BOOL | Wrk_bOutputMask[3].0 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_3_01 | Output | REAL | Wrk_Outputs[25] | 0 | Float | 0 | 0 | Bank 3 Output 1 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_3_01_EN | Output | BOOL | Wrk_bOutputMask[3].1 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_3_02 | Output | REAL | Wrk_Outputs[26] | 0 | Float | 0 | 0 | Bank 3 Output 2 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_3_02_EN | Output | BOOL | Wrk_bOutputMask[3].2 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_3_03 | Output | REAL | Wrk_Outputs[27] | 0 | Float | 0 | 0 | Bank 3 Output 3 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_3_03_EN | Output | BOOL | Wrk_bOutputMask[3].3 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_3_04 | Output | REAL | Wrk_Outputs[28] | 0 | Float | 0 | 0 | Bank 3 Output 4 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_3_04_EN | Output | BOOL | Wrk_bOutputMask[3].4 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_3_05 | Output | REAL | Wrk_Outputs[29] | 0 | Float | 0 | 0 | Bank 3 Output 5 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_3_05_EN | Output | BOOL | Wrk_bOutputMask[3].5 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_3_06 | Output | REAL | Wrk_Outputs[30] | 0 | Float | 0 | 0 | Bank 3 Output 6 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_3_06_EN | Output | BOOL | Wrk_bOutputMask[3].6 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_3_07 | Output | REAL | Wrk_Outputs[31] | 0 | Float | 0 | 0 | Bank 3 Output 7 | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Out_3_07_EN | Output | BOOL | Wrk_bOutputMask[3].7 | 0 | Decimal | 0 | 0 | Working Output Mask | Read Only | 0 | 0
raP_Opr_SeqRealOut | Out_HasScaling | Output | BOOL |  | 0 | Decimal | 0 | 0 | One or more Real outputs are configured to be scaled | Read/Write | 0 | 0
raP_Opr_SeqRealOut | Sts_ErrStepSize | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Step array is an invalid size | Read Only | 0 | 0
raP_Opr_SeqRealOut | Sts_ErrOutOfRange | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Inp_StepAbs is out of range | Read Only | 0 | 0
raP_Opr_SeqRealOut | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 1 | 1 - An error is present | Read Only | 0 | 0
raP_Tec_SeqCore | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Tec_SeqCore | Val_CurrState | Output | SINT |  | 0 | Decimal | 0 | 0 | Numerical value of the current state | Read Only | 0 | 0
raP_Tec_SeqCore | Val_StepInState | Output | INT |  | 0 | Decimal | 0 | 0 | Numerical value of the current state relative step | Read/Write | 0 | 0
raP_Tec_SeqCore | Val_StepAbs | Output | INT | Wrk_CurrStepAbs | 0 | Decimal | 0 | 0 | Numerical value of the absolute step | Read Only | 0 | 0
raP_Tec_SeqCore | Val_NextStepAbs | Output | INT |  | 0 | Decimal | 0 | 0 | Numerical value of the next absolute step | Read Only | 0 | 0
raP_Tec_SeqCore | Val_NextState | Output | SINT |  | 0 | Decimal | 0 | 0 | Numerical value of next state | Read Only | 0 | 0
raP_Tec_SeqCore | Val_NextStepInState | Output | INT |  | 0 | Decimal | 0 | 0 | Numerical value of next step in state | Read Only | 0 | 0
raP_Tec_SeqCore | Val_MaxStepIndex | Output | INT |  | 0 | Decimal | 0 | 0 | Numerical value of the last step array index | Read Only | 0 | 0
raP_Tec_SeqCore | Val_TimeDiff | Output | DINT |  | 0 | Decimal | 0 | 0 | Time differential since the last execution (mSec) | Read Only | 0 | 0
raP_Tec_SeqCore | Val_InSeqTime | Output | LINT |  | 0 | Decimal | 0 | 0 | Time in current sequence (not in state 0) (mSec) | Read/Write | 0 | 0
raP_Tec_SeqCore | Val_InPauseTime | Output | LINT |  | 0 | Decimal | 0 | 0 | Time in current pause (mSec) | Read/Write | 0 | 0
raP_Tec_SeqCore | ORdy_SeqAutoPause | Output | BOOL |  | 0 | Decimal | 0 | 0 | Auto Pause HMI Ready | Read Only | 0 | 0
raP_Tec_SeqCore | ORdy_SeqCancelPause | Output | BOOL |  | 0 | Decimal | 0 | 0 | Cancel Pause HMI Ready | Read Only | 0 | 0
raP_Tec_SeqCore | ORdy_SeqPause | Output | BOOL |  | 0 | Decimal | 0 | 0 | Pause HMI Ready | Read Only | 0 | 0
raP_Tec_SeqCore | ORdy_SeqResume | Output | BOOL |  | 0 | Decimal | 0 | 0 | Resume HMI Ready | Read Only | 0 | 0
raP_Tec_SeqCore | Out_StateComplete | Output | BOOL |  | 0 | Decimal | 0 | 1 | Current state is complete | Read Only | 0 | 0
raP_Tec_SeqCore | Sts_StateChange | Output | BOOL |  | 0 | Decimal | 0 | 0 | State has changed | Read Only | 0 | 0
raP_Tec_SeqCore | Sts_StepChange | Output | BOOL | Wrk_StepChange | 0 | Decimal | 0 | 0 | Step has changed | Read Only | 0 | 0
raP_Tec_SeqCore | Sts_Paused | Output | BOOL | Wrk_PauseBits.4 | 0 | Decimal | 0 | 0 | Sequence is paused | Read/Write | 0 | 0
raP_Tec_SeqCore | Sts_MaintByp | Output | BOOL |  | 0 | Decimal | 0 | 0 | A maintenance bypass is active | Read Only | 0 | 0
raP_Tec_SeqCore | Sts_StepTimerQualified | Output | BOOL |  | 0 | Decimal | 0 | 0 | Current step timer is qualified | Read Only | 0 | 0
raP_Tec_SeqCore | Sts_PromptQualified | Output | BOOL |  | 0 | Decimal | 0 | 0 | Current prompt is qualified | Read Only | 0 | 0
raP_Tec_SeqCore | Sts_ErrStateInp | Output | BOOL |  | 0 | Decimal | 0 | 0 | Inp_State is out of range | Read/Write | 0 | 0
raP_Tec_SeqCore | Sts_ErrStepSize | Output | BOOL |  | 0 | Decimal | 0 | 0 | Step array is of an invalid size | Read/Write | 0 | 0
raP_Tec_SeqCore | Sts_ErrStateSynch | Output | BOOL |  | 0 | Decimal | 0 | 0 | States and Steps are not synchronized | Read Only | 0 | 0
raP_Tec_SeqCore | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 0 | An error is present | Read Only | 0 | 0
raP_Tec_SeqEdit | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Tec_SeqEdit | Rdy_AddStep | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Conditions are appropriate to add a step | Read/Write | 0 | 0
raP_Tec_SeqEdit | Rdy_InsertStep | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Conditions are appropriate to insert a step | Read/Write | 0 | 0
raP_Tec_SeqEdit | Rdy_DeleteStep | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Conditions are appropriate to delete a step | Read/Write | 0 | 0
raP_Tec_SeqEdit | Rdy_Edit | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Editing is possible under the current conditions | Read Only | 0 | 0
raP_Tec_SeqEdit | Sts_ErrStateOutOfRange | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - State input value is out of range | Read Only | 0 | 0
raP_Tec_SeqEdit | Sts_ErrStepSize | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Step array is an invalid size | Read/Write | 0 | 0
raP_Tec_SeqEdit | Sts_ErrStateSynch | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - Steps and States are not synchronized | Read Only | 0 | 0
raP_Tec_SeqEdit | Sts_Err | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 - An error is present | Read Only | 0 | 0
raP_Tec_SeqEdit | Val_EditStepAbs | Output | DINT |  | 0 | Decimal | 0 | 0 | Absolute Step Number of the edit | Read Only | 0 | 0
raP_Tec_SeqEdit | Val_EditStepNextAbs | Output | DINT |  | 0 | Decimal | 0 | 0 | The step following the step to edit | Read Only | 0 | 0
raP_Tec_SeqEdit | Val_EditStepPrevAbs | Output | DINT |  | 0 | Decimal | 0 | 0 | The step before the step to edit | Read Only | 0 | 0
raP_Tec_SeqEdit | Val_NumStepsInEditState | Output | DINT |  | 0 | Decimal | 0 | 0 | Number of steps in the edit state | Read Only | 0 | 0
raP_Opr_VSM | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Opr_VSM | Sts_CmdEnable | Output | DINT |  | 0 | Decimal | 0 | 0 | Bit mapped commands enabled | Read Only | 0 | 0
raP_Opr_VSM | Sts_CmdIPInh | Output | DINT |  | 0 | Decimal | 0 | 0 | Bit mapped commands that are currently interlock inhibited | Read/Write | 0 | 0
raP_Opr_VSM | ORdy_CmdEnable | Output | DINT |  | 0 | Decimal | 0 | 0 | Bit mapped Oper commands enabled | Read Only | 0 | 0
raP_Opr_VSM | XRdy_CmdEnable | Output | DINT |  | 0 | Decimal | 0 | 0 | Bit mapped External commands enabled | Read Only | 0 | 0
raP_Opr_VSM | bState | Output | DINT |  | 1 | Decimal | 0 | 0 | Bit mapped current state | Read/Write | 0 | 0
raP_Opr_VSM | eState | Output | SINT |  | 0 | Decimal | 0 | 1 | Number of current state | Read/Write | 0 | 0
raP_Opr_VSM | Sts_State_0 | Output | BOOL | Wrk_State.0 | 0 | Decimal | 0 | 0 | 1 - Current state is the zero state | Read Only | 0 | 0
raP_Opr_VSM | MRdy_Bypass | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for MCmd_Bypass, enable HMI button. | Read Only | 0 | 0
raP_Opr_VSM | MRdy_Check | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Ready for MCmd_Check, enable HMI button. | Read Only | 0 | 0
raP_Opr_VSM | Sts_IntlkTrip | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = An interlock is Not OK. | Read Only | 0 | 0
raP_Opr_VSM | Sts_NrdyIntlk | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready: Interlock not OK. | Read Only | 0 | 0
raP_Opr_VSM | Sts_NrdyPerm | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready: Permissive not OK. | Read Only | 0 | 0
raP_Opr_VSM | Sts_NotRdy | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device is not ready, see detail bits (Sts_Nrdyxxx) for reason. | Read/Write | 0 | 0
raP_Opr_VSM | Sts_StateChg | Output | BOOL |  | 0 | Decimal | 0 | 0 | ONS when state changes | Read/Write | 0 | 0
raP_Opr_VSM | Sts_Bypass | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Bypassable interlocks are bypassed. | Read Only | 0 | 0
raP_Opr_VSM | Sts_BypActive | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Interlock bypassing active (bypassed or maintenance). | Read Only | 0 | 0
raP_Opr_VSM | Sts_MaintByp | Output | BOOL |  | 0 | Decimal | 0 | 0 | 1 = Device has a maintenance bypass function active. | Read Only | 0 | 0
raP_Opr_VSM | Ref_SMCfgPath | Output | BOOL |  | 0 | Decimal | 0 | 0 | Populate the Description field for the path to the configuration UDT instance for the HMI | Read Only | 0 | 0
raP_Tec_EventQLoad | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0
raP_Tec_EventQUnload | EnableOut | Output | BOOL |  | 0 | Decimal | 0 | 0 | Enable Output - System Defined Parameter | Read Only | 0 | 0

## InOut Parameters
Library Object | InOut Parameter | Input / Output | Data Type | Alias For | Default |  |  |  | Description
raP_Dvc_D4SD | BusObj | InOut | BUS_OBJ |  |  |  | 1 | 1 | Bus component. | 0 | 1
raP_Dvc_nPos | BusObj | InOut | BUS_OBJ |  |  |  | 1 | 1 | Bus component. | 0 | 1
raP_Dvc_VlvMP | BusObj | InOut | BUS_OBJ |  |  |  | 1 | 1 | Bus component. | 0 | 1
raP_Dvc_LgxChangeDet | Ref_CLMsgCtrl | InOut | MESSAGE |  |  |  | 1 | 1 | MSG to get controller Change Log data. | 0 | 0
raP_Dvc_LgxChangeDet | Ref_CLMsgSrc | InOut | INT[8] |  |  | Decimal | 1 | 1 | Data sent in controller Change Log MSG. | 0 | 0
raP_Dvc_LgxChangeDet | Ref_CLMsgDest | InOut | SINT[46] |  |  | Decimal | 1 | 1 | Data received in controller Change Log MSG. | 0 | 0
raP_Dvc_LgxChangeDet | Ref_CSMsgCtrl | InOut | MESSAGE |  |  |  | 1 | 1 | MSG to get controller Status data. | 0 | 0
raP_Dvc_LgxChangeDet | Ref_CSMsgSrc | InOut | INT[3] |  |  | Decimal | 1 | 1 | Date sent in controller Status MSG. | 0 | 0
raP_Dvc_LgxChangeDet | Ref_CSMsgDest | InOut | INT[4] |  |  | Decimal | 1 | 1 | Data received in controller Status MSG. | 0 | 0
raP_Dvc_LgxChangeDet | Ref_DTMsgCtrl | InOut | MESSAGE |  |  |  | 1 | 1 | MSG to get controller Date and Time data. | 0 | 0
raP_Dvc_LgxChangeDet | Ref_DTMsgSrc | InOut | INT[3] |  |  | Decimal | 1 | 1 | Data sent in controller Date and Time MSG. | 0 | 0
raP_Dvc_LgxChangeDet | Ref_DTMsgDest | InOut | INT[17] |  |  | Decimal | 1 | 1 | Data received in controller Date and Time MSG. | 0 | 0
raP_Dvc_LgxChangeDet | BusObj | InOut | BUS_OBJ |  |  |  | 1 | 1 | Bus component (for I/O configuration tree). | 0 | 1
raP_Dvc_LgxCPU_5x80 | Ref_Out | InOut | raP_UDT_Dvc_LgxCPU_5x80_Out |  |  |  | 1 | 1 | Tag to receive CPU data. | 0 | 0
raP_Dvc_LgxCPU_5x80 | Ref_ConnUseMSG | InOut | MESSAGE |  |  |  | 1 | 1 | Message to get Connection usage. | 0 | 0
raP_Dvc_LgxCPU_5x80 | Ref_ConnUseResp | InOut | INT[80] |  |  | Decimal | 1 | 1 | Connection usage response data from MSG. | 0 | 0
raP_Dvc_LgxCPU_5x80 | Ref_CoreUseMSG | InOut | MESSAGE |  |  |  | 1 | 1 | Message to get CPU usage for each core. | 0 | 0
raP_Dvc_LgxCPU_5x80 | Ref_CoreUseResp | InOut | SINT[20] |  |  | Decimal | 1 | 1 | Core CPU usage response data from MSG. | 0 | 0
raP_Dvc_LgxCPU_5x80 | Ref_TaskUseMSG | InOut | MESSAGE |  |  |  | 1 | 1 | Message to get CPU usage for each task. | 0 | 0
raP_Dvc_LgxCPU_5x80 | Ref_TaskUseRqst | InOut | DINT[2] |  |  | Decimal | 1 | 1 | Task CPU usage request data for MSG | 0 | 0
raP_Dvc_LgxCPU_5x80 | Ref_TaskUseResp | InOut | INT[100] |  |  | Decimal | 1 | 1 | Task CPU usage response data from MSG. | 0 | 0
raP_Dvc_LgxCPU_5x80 | Ref_TrendUseMSG | InOut | MESSAGE |  |  |  | 1 | 1 | Message to get Trend usage. | 0 | 0
raP_Dvc_LgxCPU_5x80 | Ref_TrendUseResp | InOut | INT[16] |  |  | Decimal | 1 | 1 | Trend usage response data from MSG. | 0 | 0
raP_Dvc_LgxCPU_5x80 | BusObj | InOut | BUS_OBJ |  |  |  | 1 | 1 | Bus component (for I/O configuration tree). | 0 | 1
raP_Dvc_LgxModuleSts | Ref_Module | InOut | MODULE |  |  |  | 1 | 1 | Module (from I/O Configuration tree) whose connection status is generated. | 0 | 0
raP_Dvc_LgxModuleSts | BusObj | InOut | BUS_OBJ |  |  |  | 1 | 1 | Bus component (for I/O configuration tree). | 0 | 1
raP_Dvc_LgxRedun | Ref_SyncMSG | InOut | MESSAGE |  |  |  | 1 | 1 | Message Control for MSG to sync primary to secondary. | 0 | 0
raP_Dvc_LgxRedun | Ref_SwitchoverMSG | InOut | MESSAGE |  |  |  | 1 | 1 | Message Control for MSG to initiate switchover to secondary. | 0 | 0
raP_Dvc_LgxRedun | Ref_SyncData | InOut | DINT |  |  | Decimal | 1 | 1 | Data for MSG to initiate sync of primary to secondary. | 0 | 0
raP_Dvc_LgxRedun | Ref_SwitchoverData | InOut | DINT |  |  | Decimal | 1 | 1 | Data for MSG to initiate switchover to secondary. | 0 | 0
raP_Dvc_LgxRedun | BusObj | InOut | BUS_OBJ |  |  |  | 1 | 1 | Bus component. | 0 | 1
raP_Dvc_LgxTaskMon | BusObj | InOut | BUS_OBJ |  |  |  | 1 | 1 | Bus component. | 0 | 1
raP_Opr_ArbitrationQ | Owner | InOut | raP_Opr_Owner |  |  |  | 1 | 1 | Associated Owner. | 0 | 0
raP_Opr_ArbitrationQ | OperQ | InOut | DINT[1] |  |  | Decimal | 1 | 1 | Operator queue array reference. | 0 | 1
raP_Opr_ArbitrationQ | ProgQ | InOut | DINT[1] |  |  | Decimal | 1 | 1 | Program queue array reference. | 0 | 1
raP_Opr_ArbitrationQ | ExtQ | InOut | DINT[1] |  |  | Decimal | 1 | 1 | External queue array reference. | 0 | 1
raP_Opr_ArbitrationQ | MaintQ | InOut | DINT[1] |  |  | Decimal | 1 | 1 | Maintenance queue array reference. | 0 | 1
raP_Opr_Area | Bus | InOut | raP_UDT_Opr_Bus |  |  |  | 1 | 1 | Bus component. | 0 | 0
raP_Opr_EMGen | Bus | InOut | raP_UDT_Opr_Bus |  |  |  | 1 | 1 | Bus component. | 0 | 1
raP_Opr_EMGen | ParObj | InOut | raP_UDT_Opr_ParRpt_Intfc |  |  |  | 1 | 1 | Optional parameter object interface. | 0 | 1
raP_Opr_EMGen | RptObj | InOut | raP_UDT_Opr_ParRpt_Intfc |  |  |  | 1 | 1 | Optional report object interface. | 0 | 1
raP_Opr_EMGen | SysObj | InOut | raP_UDT_Opr_System |  |  |  | 1 | 1 | System component. | 0 | 0
raP_Opr_EMGen | Ref_SM | InOut | raP_UDT_Opr_VSM_Cfg |  |  |  | 1 | 1 | Variable State Machine Configuration Parameters | 0 | 1
raP_Opr_EPGen | Ref_Phase | InOut | PHASE |  |  |  | 1 | 1 | Referenced phase. | 0 | 0
raP_Opr_EPGen | Bus | InOut | raP_UDT_Opr_Bus |  |  |  | 1 | 1 | Bus component. | 0 | 1
raP_Opr_EPGen | ParObj | InOut | raP_UDT_Opr_ParRpt_Intfc |  |  |  | 1 | 1 | Optional parameter object interface. | 0 | 1
raP_Opr_EPGen | RptObj | InOut | raP_UDT_Opr_ParRpt_Intfc |  |  |  | 1 | 1 | Optional Report object interface. | 0 | 1
raP_Opr_EPGen | SysObj | InOut | raP_UDT_Opr_System |  |  |  | 1 | 1 | System component. | 0 | 0
raP_Opr_ExtddAlm | Inp_ExtddAlmeNotify | InOut | SINT |  |  | Decimal | 1 | 1 | Extended alarms status enumerated values: 0 = Not in alarm, acknowledged, 1 = Not in alarm, unacknowledged or reset required, 2 = Low severity alarm, acknowledged, 3 = Low severity alarm, unacknowledged, 4 = Medium severity alarm, acknowledged, 5 = Medium severity alarm, unacknowledged, 6 = High severity alarm, acknowledged, 7 = High severity alarm, unacknowledged, 8 = Urgent severity alarm, acknowledged, 9 = Urgent severity alarm, unacknowledged. Highest active extended alarm value. | 0 | 0
raP_Opr_ExtddAlm | Inp_ExtddAlmDsply | InOut | DINT |  |  | Decimal | 1 | 1 | 1 = Extended alarm severity value is greatest of all extended alarms active. Each bit represents an individual alarm (0 - 31). | 0 | 0
raP_Opr_OrgScan | BusNode | InOut | raP_UDT_Opr_Bus_Node[2] |  |  |  | 1 | 1 | Node array reference. | 0 | 0
raP_Opr_OrgScan | Bus | InOut | raP_UDT_Opr_Bus[2] |  |  |  | 1 | 1 | Bus array reference. | 0 | 0
raP_Opr_OrgView | BusNode | InOut | raP_UDT_Opr_Bus_Node[1] |  |  |  | 1 | 1 | Node Array. | 0 | 0
raP_Opr_OrgView | Bus | InOut | raP_UDT_Opr_Bus[2] |  |  |  | 1 | 1 | Bus Array. | 0 | 0
raP_Opr_OrgView | OrgScan | InOut | raP_Opr_OrgScan |  |  |  | 1 | 1 | Associated Organization Scan. | 0 | 0
raP_Opr_Owner | none
raP_Opr_Prompt | Prompts | InOut | raP_UDT_Opr_PromptCfg[1] |  |  |  | 1 | 1 | Prompt Instance Configuration Data | 0 | 0
raP_Opr_Prompt | RespData | InOut | raP_UDT_Opr_PromptResp |  |  |  | 1 | 1 | Operator-Entered Prompt Response Data (as Strings) | 0 | 0
raP_Opr_Prompt | BusObj | InOut | BUS_OBJ |  |  |  | 1 | 1 | Bus component. | 0 | 1
raP_Opr_Prompt_Core | Prompts | InOut | raP_UDT_Opr_PromptCfg[1] |  |  |  | 1 | 1 | Prompt Instance Configuration Data | 0 | 0
raP_Opr_Prompt_Core | RespData | InOut | raP_UDT_Opr_PromptResp |  |  |  | 1 | 1 | Structure to Hold Most Recent Response Data in Character Format. | 0 | 0
raP_Opr_Unit | Bus | InOut | raP_UDT_Opr_Bus |  |  |  | 1 | 1 | Bus component. | 0 | 0
raP_Opr_Unit | BatchIntfc | InOut | raP_UDT_Opr_PUnitFTBatch_Intfc |  |  |  | 1 | 1 | Batch Interface | 0 | 1
raP_Opr_Unit | ParObj | InOut | raP_UDT_Opr_ParRpt_Intfc |  |  |  | 1 | 1 | Optional parameter object interface. | 0 | 1
raP_Opr_Unit | RptObj | InOut | raP_UDT_Opr_ParRpt_Intfc |  |  |  | 1 | 1 | Optional report object interface. | 0 | 1
raP_Tec_HARTChanData_to_PAH | HART_ChanData | InOut | HART_ChanData |  |  |  | 1 | 1 | HART channel data member from Library 4.10 module AOI. | 0 | 0
raP_Tec_HARTChanData_to_PAH | PAX_HART_DEVICE | InOut | PAX_HART_DEVICE:I:0 |  |  |  | 1 | 1 | HART channel data to PAH instruction. | 0 | 0
raP_Tec_LgxEvent | none
raP_Tec_ParRpt | Cfg_Enum | InOut | STRING[50] |  |  |  | 1 | 1 | Enumeration text set. | 0 | 1
raP_Tec_ParRpt | PSet_E | InOut | DINT |  |  | Decimal | 1 | 1 | Program issued setting of enumeration parameter value. | 0 | 1
raP_Tec_ParRpt | PSet_I | InOut | DINT |  |  | Decimal | 1 | 1 | Program issued setting of integer parameter value. | 0 | 1
raP_Tec_ParRpt | PSet_R | InOut | REAL |  |  | Float | 1 | 1 | Program issued setting of real parameter value. | 0 | 1
raP_Tec_ParRpt | PSet_S | InOut | STRING |  |  |  | 1 | 1 | Program issued setting of string parameter value. | 0 | 1
raP_Tec_ParRpt | Val_Initial_S | InOut | STRING |  |  |  | 1 | 1 | Initial string parameter value, while Inp_Trgr = 1, Val_Initial is set to the string parameter setpoint. | 0 | 1
raP_Tec_ParRpt | ParObj | InOut | raP_UDT_Opr_ParRpt_Intfc |  |  |  | 1 | 1 | Parameter object link to equipment. | 0 | 1
raP_Tec_ParRpt | RptObj | InOut | raP_UDT_Opr_ParRpt_Intfc |  |  |  | 1 | 1 | Report object link to equipment. | 0 | 1
raP_Opr_Seq | Ref_Steps | InOut | raP_UDT_Opr_SeqStep[2] |  |  |  | 1 | 1 | Data for one raP_Opr_Seq Sequencer Step | 0 | 0
raP_Opr_Seq | Bus | InOut | raP_UDT_Opr_Bus |  |  |  | 1 | 1 | Bus component | 0 | 1
raP_Opr_SeqBoolInp | Ref_Steps | InOut | raP_UDT_Opr_SeqStep[2] |  |  |  | 1 | 1 | Data for one raP_Opr_Seq Sequencer Step | 0 | 0
raP_Opr_SeqBoolOut | Ref_Steps | InOut | raP_UDT_Opr_SeqStep[2] |  |  |  | 1 | 1 | Data for one raP_Opr_Seq Sequencer Step | 0 | 0
raP_Opr_SeqRealOut | Ref_Steps | InOut | raP_UDT_Opr_SeqStep[2] |  |  |  | 1 | 1 | Data for one raP_Opr_Seq Sequencer Step | 0 | 0
raP_Tec_SeqCore | Ref_States | InOut | raP_UDT_Opr_SeqState[1] |  |  |  | 1 | 1 | Data for one raP_Opr_Seq State | 0 | 0
raP_Tec_SeqCore | Ref_Steps | InOut | raP_UDT_Opr_SeqStep[2] |  |  |  | 1 | 1 | Data for one raP_Opr_Seq Sequencer Step | 0 | 0
raP_Tec_SeqEdit | Ref_States | InOut | raP_UDT_Opr_SeqState[1] |  |  |  | 1 | 1 | Data for one raP_Opr_Seq State | 0 | 0
raP_Tec_SeqEdit | Ref_Steps | InOut | raP_UDT_Opr_SeqStep[2] |  |  |  | 1 | 1 | Data for one raP_Opr_Seq Sequencer Step | 0 | 0
raP_Opr_VSM | Cfg_SM | InOut | raP_UDT_Opr_VSM_Cfg |  |  |  | 1 | 1 | External configuration UDT | 0 | 0
raP_Tec_EventQLoad | Type | InOut | STRING_16 |  |  |  | 1 | 1 | Type used in processing current record. | 0 | 0
raP_Tec_EventQLoad | Data | InOut | String_EventQData |  |  |  | 1 | 1 | User event data as a String. | 0 | 0
raP_Tec_EventQLoad | EQ_Ctrl | InOut | EQ_Control |  |  |  | 1 | 1 | Event Queue control structure. Need one control structure per event queue. | 0 | 0
raP_Tec_EventQLoad | EQ_Recs | InOut | EQ_Record[1] |  |  |  | 1 | 1 | Event Queue record structure. An array of these records constitutes one event queue. | 0 | 0
raP_Tec_EventQUnload | EQ_Ctrl | InOut | EQ_Control |  |  |  | 1 | 1 | Event Queue control structure. Need one control structure per event queue. | 0 | 0
raP_Tec_EventQUnload | EQ_Recs | InOut | EQ_Record[1] |  |  |  | 1 | 1 | Event Queue record structure. An array of these records constitutes one event queue. | 0 | 0

## Local Tags
Library Object | Tag Name | Data Type | Default | STYLE | Description
PAH | Val_HARTRevision | SINT | 0 | Decimal | HART Spec major revision received from device. | Read Only
PAH | Sts_sHARTQVEU | STRING_16 | '' |  | Text of HART digital QV$'s engineering units. | Read Only
PAH | Sts_sHARTTVEU | STRING_16 | '' |  | Text of HART digital TV$'s engineering units. | Read Only
PAH | Sts_sHARTSVEU | STRING_16 | '' |  | Text of HART digital SV$'s engineering units. | Read Only
PAH | Sts_sHARTPVEU | STRING_16 | '' |  | Text of HART digital PV$'s engineering units. | Read Only
PAH | Sts_sPVEU | STRING_16 | '' |  | Text of analog PV$'s engineering units. | Read Only
PAH | Sts_sHARTDiagMsg3 | STRING_32 | '' |  | HART device diagnostic message #3. | Read Only
PAH | Sts_sHARTDiagMsg2 | STRING_32 | '' |  | HART device diagnostic message #2. | Read Only
PAH | Sts_sHARTDiagMsg1 | STRING_32 | '' |  | HART device diagnostic message #1. | Read Only
PAH | Sts_sHARTTag | STRING_32 | '' |  | Tag text from HART device. | Read Only
PAH | Sts_sHARTDesc | STRING_16 | '' |  | Description text from HART device. | Read Only
PAH | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
PAH | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
PAH | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance command to select Virtual (simulated) device operation. The instruction clears this operand automatically. | Read/Write
PAH | MCmd_Physical | BOOL | 0 | Decimal | Maintenance command to select Physical device operation (not simulated). The instruction clears this operand automatically. | Read/Write
PAI | MSet_SubstPV | REAL | 0 | Float | Maintenance-entered substitute PV in engineering units that overrides input PV when MCmd_SubstPV is 1. If not using the substitute (MCmd_SubstPV is false), the MSet_SubstPV setting tracks the Out value for bumpless transfer from input PV to substitute PV. | Read/Write
PAI | MCmd_SubstPV | BOOL | 0 | Decimal | Maintenance command to use substitute PV. The instruction clears this operand automatically. | Read/Write
PAI | MCmd_InpPV | BOOL | 0 | Decimal | Maintenance command to use input PV (normal). The instruction clears this operand automatically. | Read/Write
PAI | OCmd_ClearCapt | BOOL | 0 | Decimal | Operator command to clear the captured minimum/maximum PV excursion values. The instruction clears this operand automatically. | Read/Write
PAI | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write
PAI | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to acknowledge and reset all alarms and latched shed conditions. The use of OCmd_ResetAckAll is restricted to HMI. The instruction clears this operand automatically. | Read/Write
PAI | MRdy_SubstPV | BOOL | 0 | Decimal | 1 = The instruction is ready for SubstPV command. | Read Only
PAI | MRdy_InpPV | BOOL | 0 | Decimal | 1 = The instruction is ready for MCmd_InpPV command. | Read Only
PAI | ORdy_ClearCapt | BOOL | 0 | Decimal | 1 = Ready for OCmd_ClearCapt, enable HMI button. | Read Only
PAI | ORdy_Reset | BOOL | 0 | Decimal | 1 = A latched alarm or shed condition is ready to be reset. | Read Only
PAI | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = A latched alarm or shed condition is ready to be reset or acknowledged. | Read Only
PAI | HMI_BusObjIndex | DINT | 0 | Decimal | HMI bus object index. | Read Only
PAI | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
PAI | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
PAI | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance command to select virtual (simulated) device operation. The instruction clears this operand automatically. | Read/Write
PAI | MCmd_Physical | BOOL | 0 | Decimal | Maintenance command to select physical device operation (not simulated). The instruction clears this operand automatically. | Read/Write
PAID | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll (enables HMI button). | Read Only
PAID | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset (enables HMI button). | Read Only
PAID | ORdy_SelMax | BOOL | 0 | Decimal | 1 = Ready for OCmd_SelMax (enables HMI button). | Read Only
PAID | ORdy_SelMin | BOOL | 0 | Decimal | 1 = Ready for OCmd_SelMin (enables HMI button). | Read Only
PAID | ORdy_SelAvg | BOOL | 0 | Decimal | 1 = Ready for OCmd_SelAvg. | Read Only
PAID | ORdy_SelB | BOOL | 0 | Decimal | 1 = Ready for OCmd_SelB (enables HMI button). | Read Only
PAID | ORdy_SelA | BOOL | 0 | Decimal | 1 = Ready for OCmd_SelA (enables HMI button). | Read Only
PAID | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to reset and acknowledge all alarms. | Read/Write
PAID | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms requiring reset. | Read/Write
PAID | OCmd_SelMax | BOOL | 0 | Decimal | Operator command to select maximum(A,B) PV. | Read/Write
PAID | OCmd_SelMin | BOOL | 0 | Decimal | Operator command to select minimum(A,B) PV. | Read/Write
PAID | OCmd_SelAvg | BOOL | 0 | Decimal | Operator command to select average(A,B) PV. | Read/Write
PAID | OCmd_SelB | BOOL | 0 | Decimal | Operator command to select sensor B PV. | Read/Write
PAID | OCmd_SelA | BOOL | 0 | Decimal | Operator command to select sensor A PV. | Read/Write
PAID | HMI_BusObjIndex | DINT | 0 | Decimal | HMI bus object index | Read/Write
PAIM | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll (enables HMI button). | Read Only
PAIM | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset (enables HMI button). | Read Only
PAIM | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to reset and acknowledge all alarms. | Read/Write
PAIM | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms requiring reset. | Read/Write
PAIM | HMI_BusObjIndex | DINT | 0 | Decimal | HMI bus object index. | Read/Write
PAO | OSet_CV | REAL | 0 | Float | Operator setting of controlled variable, output (engineering units). | Read/Write
PAO | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance command to bypass all bypassable interlocks and permissives. The instruction clears this operand automatically. | Read/Write
PAO | MCmd_Check | BOOL | 0 | Decimal | Maintenance command to bypass all bypassable interlocks and permissives. The instruction clears this operand automatically. | Read/Write
PAO | MCmd_OoS | BOOL | 0 | Decimal | Maintenance command to select Out of Service. The instruction clears this operand automatically. | Read/Write
PAO | MCmd_IS | BOOL | 0 | Decimal | Maintenance command to check (not bypass) all interlocks and permissives. The instruction clears this operand automatically. | Read/Write
PAO | MCmd_Acq | BOOL | 0 | Decimal | Maintenance command to acquire ownership (Operator/Program/External/Override to Maintenance). The instruction clears this operand automatically. | Read/Write
PAO | MCmd_Rel | BOOL | 0 | Decimal | Maintenance command to release ownership (Maintenance to Operator/Program/External/Override). The instruction clears this operand automatically. | Read/Write
PAO | OCmd_BumpClose | BOOL | 0 | Decimal | Operator Command to bump device closed (used when device position feedback is not available). | Read/Write
PAO | OCmd_BumpOpen | BOOL | 0 | Decimal | Operator Command to bump device open (used when device position feedback is not available). | Read/Write
PAO | OCmd_Oper | BOOL | 0 | Decimal | Operator command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write
PAO | OCmd_Prog | BOOL | 0 | Decimal | Operator command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write
PAO | OCmd_Lock | BOOL | 0 | Decimal | Operator command to lock Operator (disallow Program). The instruction clears this operand automatically. | Read/Write
PAO | OCmd_Unlock | BOOL | 0 | Decimal | Operator command to unlock or release (allow Program to acquire) ownership. The instruction clears this operand automatically. | Read/Write
PAO | OCmd_Normal | BOOL | 0 | Decimal | Operator command to select Normal (Operator or Program). The instruction clears this operand automatically. | Read/Write
PAO | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write
PAO | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to acknowledge and reset all alarms and latched shed conditions. The use of OCmd_ResetAckAll is restricted to HMI. The instruction clears this operand automatically. | Read/Write
PAO | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready to receive MCmd_Bypass, enable HMI button. | Read Only
PAO | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready to receive MCmd_Check, enable HMI button. | Read Only
PAO | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
PAO | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
PAO | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
PAO | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
PAO | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
PAO | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
PAO | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
PAO | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
PAO | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
PAO | ORdy_BumpClose | BOOL | 0 | Decimal | 1 = Ready for OCmd_BumpClose, enable HMI button. | Read Only
PAO | ORdy_BumpOpen | BOOL | 0 | Decimal | 1 = Ready for OCmd_BumpOpen, enable HMI button. | Read Only
PAO | ORdy_CV | BOOL | 0 | Decimal | 1 = Ready to receive OSet_CV, enable HMI data entry field. | Read Only
PAO | ORdy_Reset | BOOL | 0 | Decimal | 1 = A latched alarm or shed condition is ready to be reset. | Read Only
PAO | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = A latched alarm or shed condition is ready to be reset or acknowledged. | Read Only
PAO | CmdSrc | P_COMMAND_SOURCE | 0 |  |  | Read/Write
PAO | Wrk_DevT | TIMER | {...} |  | Timer for deviation status. | Read Only
PAO | HMI_BusObjIndex | DINT | 0 | Decimal | HMI bus object index. | Read Only
PAO | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
PAO | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance command to select Virtual (simulated) device operation. The instruction clears this operand automatically. | Read/Write
PAO | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
PAO | MCmd_Physical | BOOL | 0 | Decimal | Maintenance command to select Physical device operation (not simulated). The instruction clears this operand automatically. | Read/Write
PBL | Cfg_GateSrc4Invert | SINT | 2#0000_0000 | Binary | Gate M Source #4 is Inverted (M by bit) (1 = invert). | Read/Write
PBL | Cfg_GateSrc3Invert | SINT | 2#0000_0000 | Binary | Gate M Source #3 is Inverted (M by bit) (1 = invert). | Read/Write
PBL | Cfg_GateSrc2Invert | SINT | 2#0000_0000 | Binary | Gate M Source #2 is Inverted (M by bit) (1 = invert). | Read/Write
PBL | Cfg_GateSrc1Invert | SINT | 2#0000_0000 | Binary | Gate M Source #1 is Inverted (M by bit) (1 = invert). | Read/Write
PBL | Cfg_GateSrc4Mask | SINT | 2#0000_0000 | Binary | Gate M Source #4 is Used (M by bit) (1 = used). | Read/Write
PBL | Cfg_GateSrc3Mask | SINT | 2#0000_0000 | Binary | Gate M Source #3 is Used (M by bit) (1 = used). | Read/Write
PBL | Cfg_GateSrc2Mask | SINT | 2#0000_0000 | Binary | Gate M Source #2 is Used (M by bit) (1 = used). | Read/Write
PBL | Cfg_GateSrc1Mask | SINT | 2#0000_0000 | Binary | Gate M Source #1 is Used (M by bit) (1 = used). | Read/Write
PBL | Cfg_HasNav | SINT | 2#0000_0000 | Binary | Set bits indicate which navigation buttons are enabled. | Read/Write
PBL | Wrk_Src | INT | 2#0000_0000_0000_0000 | Binary | Working source (input and gate status) bits .0 to .15. | Read/Write
PBL | Cfg_GateSrc4Ptr | DINT[8] | {...} | Decimal | Pointer to Gate M Source #4 (0...7 = inputs, 8...15 = gate outputs). | Read/Write
PBL | Cfg_GateSrc3Ptr | DINT[8] | {...} | Decimal | Pointer to Gate M Source #3 (0...7 = inputs, 8...15 = gate outputs). | Read/Write
PBL | Cfg_GateSrc2Ptr | DINT[8] | {...} | Decimal | Pointer to Gate M Source #2 (0...7 = inputs, 8...15 = gate outputs). | Read/Write
PBL | Cfg_GateSrc1Ptr | DINT[8] | {...} | Decimal | Pointer to Gate M Source #1 (0...7 = inputs, 8...15 = gate outputs). | Read/Write
PBL | Cfg_GateFunc | DINT[8] | {…} | Decimal | Function code for gate M (1 = AND, 2 = OR, 3 = XOR, 4 = 2oo3, 5 = Set-Reset). | Read/Write
PBL | Cfg_OutSrcPtr | DINT | 0 | Decimal | Source bit for Output (0...7 = inputs, 8...15 = gates). | Read/Write
PBL | Wrk_OnDly | TIMER | {…} |  | Output ON delay timer. | Read Only
PBL | Cfg_OutSrcInvert | BOOL | 0 | Decimal | Out source (before minimum duration timer) is inverted (1 = invert). | Read/Write
PBL | Val_LastGate | DINT[8] | {…} | Decimal | Last gate pin which uses this gate result (0 = not used, 1...32 = gates, 33 = output). | Read Only
PBL | Val_LastInp | DINT[8] | {…} | Decimal | Last gate pin which uses this input (0 = not used, 1...32 = gates, 33 = output) For animation. | Read Only
PBL | HMI_Const | SINT[9] | {…} | Decimal | Constants (for use in HMI indirection of parameters). | Read Only
PBL | Val_SnapTimestamp | DINT[7] | {…} | Decimal | Snapshot timestamp [0] = year, [1] = month, [2] = day, [3] = hour, [4] = minute, [5] = second, [6] = usecond. | Read Only
PBL | Wrk_OffDly | TIMER | {…} |  | Output OFF delay timer. | Read Only
PBL | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset (enables button). | Read Only
PBL | ORdy_Snap | BOOL | 0 | Decimal | 1 =Ready for OCmd_Snap (enables button). | Read Only
PBL | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset (re-arm) snapshot latch. | Read/Write
PBL | OCmd_Snap | BOOL | 0 | Decimal | Operator Command to capture input, gate states in snapshot. | Read/Write
PD4SD | CmdSrc | P_COMMAND_SOURCE | {…} |  | Command source selection. | Read/Write
PD4SD | HMI_St3PermOK | BOOL | 0 | Decimal | 1 = Permissives are OK to go to State 3. | Read Only
PD4SD | HMI_St2PermOK | BOOL | 0 | Decimal | 1 = Permissives are OK to go to State 2. | Read Only
PD4SD | HMI_St1PermOK | BOOL | 0 | Decimal | 1 = Permissives are OK to go to State 1. | Read Only
PD4SD | HMI_St0PermOK | BOOL | 0 | Decimal | 1 = Permissives are OK to go to State 0. | Read Only
PD4SD | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll, enable HMI button. | Read Only
PD4SD | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only
PD4SD | ORdy_St3 | BOOL | 0 | Decimal | 1 = Ready for OCmd_St3, enable HMI button. | Read Only
PD4SD | ORdy_St2 | BOOL | 0 | Decimal | 1 = Ready for OCmd_St2, enable HMI button. | Read Only
PD4SD | ORdy_St1 | BOOL | 0 | Decimal | 1 = Ready for OCmd_St1, enable HMI button. | Read Only
PD4SD | ORdy_St0 | BOOL | 0 | Decimal | 1 = Ready for OCmd_St0, enable HMI button. | Read Only
PD4SD | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready for MCmd_Check, enable HMI button. | Read Only
PD4SD | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready for MCmd_Bypass, enable HMI button. | Read Only
PD4SD | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator Command to acknowledge all alarms and reset latched alarms and shed conditions. The instruction clears this operand automatically. | Read/Write
PD4SD | OCmd_Reset | BOOL | 0 | Decimal | Operator Command to reset shed latches and returned-to-normal latched alarms. The instruction clears this operand automatically. | Read/Write
PD4SD | OCmd_St3 | BOOL | 0 | Decimal | Operator Command to set device to State 3. The instruction clears this operand automatically. | Read/Write
PD4SD | OCmd_St2 | BOOL | 0 | Decimal | Operator Command to set device to State 2. The instruction clears this operand automatically. | Read/Write
PD4SD | OCmd_St1 | BOOL | 0 | Decimal | Operator Command to set device to State 1. The instruction clears this operand automatically. | Read/Write
PD4SD | OCmd_St0 | BOOL | 0 | Decimal | Operator Command to set device to State 0. The instruction clears this operand automatically. | Read/Write
PD4SD | MCmd_Check | BOOL | 0 | Decimal | Maintenance Command to remove bypass and check all interlocks and permissives. The instruction clears this operand automatically. | Read/Write
PD4SD | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance Command to bypass all bypassable interlocks and permissives. The instruction clears this operand automatically. | Read/Write
PD4SD | OCmd_Unlock | BOOL | 0 | Decimal | Operator Command to unlock Operator command source and allow Program to acquire. The instruction clears this operand automatically. | Read/Write
PD4SD | OCmd_Prog | BOOL | 0 | Decimal | Operator Command to select Program (unlocked) command source. The instruction clears this operand automatically. | Read/Write
PD4SD | OCmd_Oper | BOOL | 0 | Decimal | Operator Command to select Operator (unlocked) command source. The instruction clears this operand automatically. | Read/Write
PD4SD | OCmd_Normal | BOOL | 0 | Decimal | Operator Command to select configured normal command source (Operator or Program). The instruction clears this operand automatically. | Read/Write
PD4SD | OCmd_Lock | BOOL | 0 | Decimal | Operator Command to select Operator Locked command source and disallow Program. The instruction clears this operand automatically. | Read/Write
PD4SD | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
PD4SD | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
PD4SD | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
PD4SD | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
PD4SD | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
PD4SD | MCmd_OoS | BOOL | 0 | Decimal | Maintenance Command to select Out of Service. The instruction clears this operand automatically. | Read/Write
PD4SD | MCmd_IS | BOOL | 0 | Decimal | Maintenance Command to select In Service. The instruction clears this operand automatically. | Read/Write
PD4SD | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
PD4SD | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
PD4SD | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
PD4SD | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
PD4SD | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
PD4SD | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
PD4SD | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance Command to select Virtual device operation. The instruction clears this operand automatically. | Read/Write
PD4SD | MCmd_Physical | BOOL | 0 | Decimal | Maintenance Command to select Physical device operation. The instruction clears this operand automatically. | Read/Write
PD4SD | MCmd_Rel | BOOL | 0 | Decimal | Maintenance Command to release Maintenance command source. The instruction clears this operand automatically. | Read/Write
PD4SD | MCmd_Acq | BOOL | 0 | Decimal | Maintenance Command to acquire Maintenance command source. The instruction clears this operand automatically. | Read/Write
PD4SD | HMI_BusObjIndex | DINT | 0 | Decimal | This object$'s index in the bus array, for use by HMI display. | Read Only
PD4SD | HMI_eCmdState | SINT | 0 | Decimal | Device target state: 0 = None, 1 = State 0, 2 = State 1, 3 = State 2, 4 = State 3. | Read Only
PDBC | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to reset shed latches and cleared alarms, plus acknowledge alarms. | Read/Write
PDBC | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset shed latches and cleared alarms. | Read/Write
PDBC | OCmd_Man | BOOL | 0 | Decimal | Operator command to select manual loop mode. | Read/Write
PDBC | OCmd_Auto | BOOL | 0 | Decimal | Operator command to select automatic loop mode. | Read/Write
PDBC | OCmd_None | BOOL | 0 | Decimal | Operator command to clear raise, lower outputs (in manual). | Read/Write
PDBC | OCmd_Lower | BOOL | 0 | Decimal | Operator command to set output to lower (in manual). | Read/Write
PDBC | OCmd_Raise | BOOL | 0 | Decimal | Operator command to set output to raise (in manual). | Read/Write
PDBC | OSet_RaiseSP | REAL | 20 | Float | Operator setting for raise setpoint (engineering units). Valid = Any float from Cfg_SPLoLim to Cfg_SPHiLim. | Read/Write
PDBC | OSet_LowerSP | REAL | 30 | Float | Operator setting for lower setpoint (engineering units). Valid = Any float from Cfg_SPLoLim to Cfg_SPHiLim. | Read/Write
PDBC | ORdy_SP | BOOL | 0 | Decimal | 1 = Ready for Setpoint OSets (enables data entry fields). | Read Only
PDBC | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll, enables HMI button. | Read Only
PDBC | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enables HMI button. | Read Only
PDBC | ORdy_Man | BOOL | 0 | Decimal | 1 = Ready for OCmd_Man. | Read Only
PDBC | ORdy_Auto | BOOL | 0 | Decimal | 1 = Ready for OCmd_Auto. | Read Only
PDBC | ORdy_None | BOOL | 0 | Decimal | 1 = Ready for OCmd_None. | Read Only
PDBC | ORdy_Lower | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lower. | Read Only
PDBC | ORdy_Raise | BOOL | 0 | Decimal | 1 = Ready for OCmd_Raise. | Read Only
PDBC | Wrk_ErrTimer | BOOL | 0 | Decimal | 1 = Error in configuration: Invalid timer preset (use 0 to 2147483), working copy. | Read/Write
PDBC | CmdSrc | P_COMMAND_SOURCE | {...} |  |  | Read/Write
PDBC | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
PDBC | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
PDBC | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
PDBC | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
PDBC | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
PDBC | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
PDBC | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
PDBC | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
PDBC | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
PDBC | MCmd_IS | BOOL | 0 | Decimal | Maintenance command to select in service. The instruction clears this operand automatically. | Read/Write
PDBC | MCmd_OoS | BOOL | 0 | Decimal | Maintenance command to select out of service. The instruction clears this operand automatically. | Read/Write
PDBC | MCmd_Rel | BOOL | 0 | Decimal | Maintenance command to release ownership (maintenance to operator / program / external / override). The instruction clears this operand automatically. | Read/Write
PDBC | OCmd_Lock | BOOL | 0 | Decimal | Operator command to lock operator (disallow program). The instruction clears this operand automatically. | Read/Write
PDBC | OCmd_Normal | BOOL | 0 | Decimal | Operator command to select normal (operator or program). The instruction clears this operand automatically. | Read/Write
PDBC | OCmd_Oper | BOOL | 0 | Decimal | Operator command to select operator (program to operator). The instruction clears this operand automatically. | Read/Write
PDBC | OCmd_Prog | BOOL | 0 | Decimal | Operator command to select program (operator to program). The instruction clears this operand automatically. | Read/Write
PDBC | OCmd_Unlock | BOOL | 0 | Decimal | Operator command to unlock or release ownership and allow program to acquire ownership. The instruction clears this operand automatically. | Read/Write
PDBC | MCmd_Acq | BOOL | 0 | Decimal | Maintenance command to acquire ownership (operator / program / external / override to maintenance). The instruction clears this operand automatically. | Read/Write
PDBC | HMI_BusObjIndex | DINT | 0 | Decimal | HMI bus object index | Read/Write
PDI | MSet_SubstPV | BOOL | 0 | Decimal | Maintenance-entered substitute PV that overrides input PV when Sts_SubstPV is 1. If not using the substitute (Sts_SubstPV is false), the MSet_SubstPV setting tracks the Out value for bumpless transfer from input PV to substitute PV. | Read/Write
PDI | MCmd_SubstPV | BOOL | 0 | Decimal | Maintenance command to use Substitute PV (Override input). The instruction clears this operand automatically. | Read/Write
PDI | MCmd_InpPV | BOOL | 0 | Decimal | Maintenance command to use Input PV (Normal). The instruction clears this operand automatically. | Read/Write
PDI | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write
PDI | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to acknowledge and reset all alarms and latched shed conditions. The use of OCmd_ResetAckAll is restricted to HMI. The instruction clears this operand automatically. | Read/Write
PDI | MRdy_SubstPV | BOOL | 0 | Decimal | 1 = The instruction is ready for SubstPV command. | Read Only
PDI | MRdy_InpPV | BOOL | 0 | Decimal | 1 = The instruction is ready for InpPV command. | Read Only
PDI | ORdy_Reset | BOOL | 0 | Decimal | 1 = A latched alarm or shed condition is ready to be reset. | Read Only
PDI | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = A latched alarm or shed condition is ready to be reset or acknowledged. | Read Only
PDI | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance command to select Virtual (simulated) device operation. The instruction clears this operand automatically. | Read/Write
PDI | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
PDI | MCmd_Physical | BOOL | 0 | Decimal | Maintenance command to select Physical device operation (not simulated). The instruction clears this operand automatically. | Read/Write
PDI | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
PDI | Wrk_TgtDisagreeOffDlyT | TIMER | {...} |  | Target disagree off delay gate timer. | Read Only
PDI | Wrk_TgtDisagreeOnDlyT | TIMER | {...} |  | Target disagree on delay gate timer. | Read Only
PDI | HMI_BusObjIndex | DINT | 0 | Decimal | This object$'s index in the bus array, for use by HMI display. | Read Only
PDO | CmdSrc | P_COMMAND_SOURCE | {...} |  |  | Read/Write
PDO | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance command to bypass all bypassable interlocks and permissives. The instruction clears this operand automatically. | Read/Write
PDO | MCmd_Check | BOOL | 0 | Decimal | Maintenance command to check (not bypass) all interlocks and permissives. The instruction clears this operand automatically. | Read/Write
PDO | MCmd_OoS | BOOL | 0 | Decimal | Maintenance command to select Out of Service. The instruction clears this operand automatically. | Read/Write
PDO | MCmd_IS | BOOL | 0 | Decimal | Maintenance command to select In Service. The instruction clears this operand automatically. | Read/Write
PDO | MCmd_Acq | BOOL | 0 | Decimal | Maintenance command to acquire ownership (Operator/Program/External/Override to Maintenance). The instruction clears this operand automatically. | Read/Write
PDO | OCmd_On | BOOL | 0 | Decimal | Operator command to turn device On. The instruction clears this operand automatically. | Read/Write
PDO | OCmd_Off | BOOL | 0 | Decimal | Operator command to turn device Off. The instruction clears this operand automatically. | Read/Write
PDO | OCmd_OnPulse | BOOL | 0 | Decimal | Operator command to pulse device that is Off, On once. The instruction clears this operand automatically. | Read/Write
PDO | OCmd_OffPulse | BOOL | 0 | Decimal | Operator command to pulse device that is On, Off once. The instruction clears this operand automatically. | Read/Write
PDO | OCmd_ContPulse | BOOL | 0 | Decimal | Operator command to pulse device continuously (blink). The instruction clears this operand automatically. | Read/Write
PDO | OCmd_Oper | BOOL | 0 | Decimal | Operator command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write
PDO | OCmd_Prog | BOOL | 0 | Decimal | Operator command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write
PDO | OCmd_Lock | BOOL | 0 | Decimal | Operator command to lock Operator (disallow Program). The instruction clears this operand automatically. | Read/Write
PDO | OCmd_Normal | BOOL | 0 | Decimal | Operator command to select Normal (Operator or Program). The instruction clears this operand automatically. | Read/Write
PDO | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write
PDO | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to acknowledge and reset all alarms and latched shed conditions. The use of OCmd_ResetAckAll is restricted to HMI. The instruction clears this operand automatically. | Read/Write
PDO | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready for MCmd_Bypass, enable HMI button. | Read Only
PDO | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready for MCmd_Check, enable HMI button. | Read Only
PDO | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
PDO | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
PDO | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
PDO | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
PDO | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
PDO | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
PDO | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
PDO | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
PDO | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
PDO | ORdy_On | BOOL | 0 | Decimal | 1 = Ready for OCmd_On, enable HMI button. | Read Only
PDO | ORdy_Off | BOOL | 0 | Decimal | 1 = Ready for OCmd_Off, enable HMI button. | Read Only
PDO | ORdy_OnPulse | BOOL | 0 | Decimal | 1 = Ready for OCmd_OnPulse, enable HMI button. | Read Only
PDO | ORdy_OffPulse | BOOL | 0 | Decimal | 1 = Ready for OCmd_OffPulse, enable HMI button. | Read Only
PDO | ORdy_ContPulse | BOOL | 0 | Decimal | 1 = Ready for OCmd_ContPulse, enable HMI button. | Read Only
PDO | ORdy_Reset | BOOL | 0 | Decimal | 1 = A latched alarm or shed condition is ready to be reset. | Read Only
PDO | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = A latched alarm or shed condition is ready to be reset or acknowledged. | Read Only
PDO | Wrk_OnT | TIMER | {...} |  | On Feedback Check Timer | Read Only
PDO | Wrk_OffT | TIMER | {...} |  | Off Feedback Check Timer | Read Only
PDO | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance command to select Virtual (simulated) device operation. The instruction clears this operand automatically. | Read/Write
PDO | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
PDO | MCmd_Physical | BOOL | 0 | Decimal | Maintenance command to select Physical device operation (not simulated). The instruction clears this operand automatically. | Read/Write
PDO | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
PDO | HMI_BusObjIndex | DINT | 0 | Decimal | This object$'s index in the bus array, for use by HMI display. | Read Only
PDO | MCmd_Rel | BOOL | 0 | Decimal | Maintenance command to release ownership (Maintenance to Operator/Program/External/Override). The instruction clears this operand automatically. | Read/Write
PDO | OCmd_Unlock | BOOL | 0 | Decimal | Operator command to unlock / release (allow Program to acquire) ownership. The instruction clears this operand automatically. | Read/Write
PDOSE | CmdSrc | P_COMMAND_SOURCE | {...} |  | Command Source | Read/Write
PDOSE | OSet_TolLo | REAL | 0 | Float | Operator setting of low tolerance limit (ok amount < SP). Valid = 0.0 to maximum positive float. | Read/Write
PDOSE | OSet_TolHi | REAL | 0 | Float | Operator setting of high tolerance limit (ok amount > SP). Valid = 0.0 to maximum positive float. | Read/Write
PDOSE | OSet_Preact | REAL | 0 | Float | Operator setting of amount before total to stop flow (Engineering Units). Valid = 0.0 to maximum positive float. | Read/Write
PDOSE | OSet_DribbleQty | REAL | 0 | Float | Operator setting of quantity to dribble (Engineering Units). Valid = 0.0 to maximum positive float. | Read/Write
PDOSE | OSet_SP | REAL | 0 | Float | Operator setting of total quantity to deliver (Engineering Units). Valid = 0.0 to maximum positive float. | Read/Write
PDOSE | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write
PDOSE | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms requiring reset. The instruction clears this operand automatically. | Read/Write
PDOSE | OCmd_Bump | BOOL | 0 | Decimal | Operator command to bump delivery for under tolerance. The instruction clears this operand automatically. | Read/Write
PDOSE | OCmd_CheckTol | BOOL | 0 | Decimal | Operator command to check tolerances. The instruction clears this operand automatically. | Read/Write
PDOSE | OCmd_StopFlow | BOOL | 0 | Decimal | Operator command to stop/pause delivery. The instruction clears this operand automatically. | Read/Write
PDOSE | OCmd_StartFlow | BOOL | 0 | Decimal | Operator command to start deliver. The instruction clears this operand automatically. | Read/Write
PDOSE | OCmd_StopTot | BOOL | 0 | Decimal | Operator command to stop totalizer. The instruction clears this operand automatically. | Read/Write
PDOSE | OCmd_StartTot | BOOL | 0 | Decimal | Operator command to start totalizer. The instruction clears this operand automatically. | Read/Write
PDOSE | OCmd_ClearTot | BOOL | 0 | Decimal | Operator command to clear totalizer quantity. The instruction clears this operand automatically. | Read/Write
PDOSE | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll (enables HMI button). | Read Only
PDOSE | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset (enables HMI button). | Read Only
PDOSE | ORdy_Bump | BOOL | 0 | Decimal | 1 = Ready for OCmd_Bump (enables HMI button). | Read Only
PDOSE | ORdy_CheckTol | BOOL | 0 | Decimal | 1 = Ready for OCmd_CheckTol (enables HMI button). | Read Only
PDOSE | ORdy_StopFlow | BOOL | 0 | Decimal | 1 = Ready for OCmd_StopFlow (enables HMI button). | Read Only
PDOSE | ORdy_StartFlow | BOOL | 0 | Decimal | 1 = Ready for OCmd_StartFlow (enables HMI button). | Read Only
PDOSE | ORdy_StopTot | BOOL | 0 | Decimal | 1 = Ready for OCmd_StopTot (enables HMI button). | Read Only
PDOSE | ORdy_StartTot | BOOL | 0 | Decimal | 1 = Ready for OCmd_StartTot (enables HMI button). | Read Only
PDOSE | ORdy_ClearTot | BOOL | 0 | Decimal | 1 = Ready for OCmd_ClearTot (enables HMI button). | Read Only
PDOSE | ORdy_Tol | BOOL | 0 | Decimal | 1 = Ready for OSet_Tol (enables HMI entry field). | Read Only
PDOSE | ORdy_DribblePreact | BOOL | 0 | Decimal | 1 = Ready for OSet_DribblePreact (enables HMI entry field). | Read Only
PDOSE | ORdy_SP | BOOL | 0 | Decimal | 1 = Ready for OSet_SP (enables HMI entry field). | Read Only
PDOSE | MCmd_Acq | BOOL | 0 | Decimal | Maintenance command to acquire ownership (Operator/Program/External/Override to Maintenance). The instruction clears this operand automatically. | Read/Write
PDOSE | MCmd_IS | BOOL | 0 | Decimal | Maintenance command to select in service. The instruction clears this operand automatically. | Read/Write
PDOSE | MCmd_OoS | BOOL | 0 | Decimal | Maintenance command to select out of service. The instruction clears this operand automatically. | Read/Write
PDOSE | MCmd_Rel | BOOL | 0 | Decimal | Maintenance command to release ownership (Maintenance to Operator/Program/External/Override). The instruction clears this operand automatically. | Read/Write
PDOSE | OCmd_Lock | BOOL | 0 | Decimal | Operator command to lock Operator (disallow Program). The instruction clears this operand automatically. | Read/Write
PDOSE | OCmd_Normal | BOOL | 0 | Decimal | Operator command to select normal (Operator or Program). The instruction clears this operand automatically. | Read/Write
PDOSE | OCmd_Oper | BOOL | 0 | Decimal | Operator command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write
PDOSE | OCmd_Prog | BOOL | 0 | Decimal | Operator command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write
PDOSE | OCmd_Unlock | BOOL | 0 | Decimal | Operator command to unlock / release (allow Program to acquire) ownership. The instruction clears this operand automatically. | Read/Write
PDOSE | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
PDOSE | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
PDOSE | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
PDOSE | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
PDOSE | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
PDOSE | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
PDOSE | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
PDOSE | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
PDOSE | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
PDOSE | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
PDOSE | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
PDOSE | MCmd_Physical | BOOL | 0 | Decimal | Maintenance command to select Physical operation (not virtualized) | Read/Write
PDOSE | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance command to select Virtual (virtualized) operation | Read/Write
PDOSE | HMI_BusObjIndex | DINT | 0 | Decimal | HMI bus object index | Read/Write
PDOSE | XRdy_Bump | BOOL | 0 | Decimal | 1 = Ready for XCmd_Bump (enables HMI button). | Read Only
PDOSE | XRdy_CheckTol | BOOL | 0 | Decimal | 1 = Ready for XCmd_Checktol (enables HMI button). | Read Only
PDOSE | XRdy_ClearTot | BOOL | 0 | Decimal | 1 = Ready for XCmd_Cleartot (enables HMI button). | Read Only
PDOSE | XRdy_DribblePreact | BOOL | 0 | Decimal | 1 = Ready for XSet_DribblePreact (enables HMI entry field). | Read Only
PDOSE | XRdy_Lock | BOOL | 0 | Decimal | 1 = Ready for XCmd_Lock, enable HMI button. | Read Only
PDOSE | XRdy_Normal | BOOL | 0 | Decimal | 1 = Ready for XCmd_Normal, enable HMI button. | Read Only
PDOSE | XRdy_Oper | BOOL | 0 | Decimal | 1 = Ready for XCmd_Oper, enable HMI button. | Read Only
PDOSE | XRdy_Prog | BOOL | 0 | Decimal | 1 = Ready for XCmd_Prog, enable HMI button. | Read Only
PDOSE | XRdy_SP | BOOL | 0 | Decimal | 1 = Ready for XSet_SP (enables HMI entry field). | Read Only
PDOSE | XRdy_StartFlow | BOOL | 0 | Decimal | 1 = Ready for XCmd_StartFlow (enables HMI button). | Read Only
PDOSE | XRdy_StartTot | BOOL | 0 | Decimal | 1 = Ready for XCmd_StartTot (enables HMI button). | Read Only
PDOSE | XRdy_StopFlow | BOOL | 0 | Decimal | 1 = Ready for XCmd_StopFlow (enables HMI button). | Read Only
PDOSE | XRdy_StopTot | BOOL | 0 | Decimal | 1 = Ready for XCmd_StopTot (enables HMI button). | Read Only
PDOSE | XRdy_Tol | BOOL | 0 | Decimal | 1 = Ready for XSet_Tol (enables HMI entry field). | Read Only
PDOSE | XRdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for XCmd_Unlock, enable HMI button. | Read Only
PDOSE | Wrk_NrdyEqpFault | BOOL | 0 | Decimal | 1 = Object not ready: External equipment fault (fault or shed requires reset). | Read Only
PDOSE | Wrk_CalcRate | BOOL | 0 | Decimal | 1 = Differentiate Inp_QtyPV to get rate, 0 = Use Inp_RatePV. | Read/Write
PDOSE | Wrk_CalcQty | BOOL | 0 | Decimal | 1 = Integrate Inp_RatePV to get quantity, 0 = Use Inp_QtyPV. | Read/Write
PDOSE | Wrk_CtrldEqpFault | BOOL | 0 | Decimal | Controlled equipment object or I/O status 0 = Ok, 1 = Fail. | Read/Write
PINTLK | Wrk_Inp | DINT | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | Collection copy of Inp_IntlkXXs. | Read/Write
PINTLK | HMI_Tab | SINT | 0 | Decimal | Tab to display (FTView ME). | Read/Write
PINTLK | MSet_Bypass | DINT | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | Individual condition maintenance bypass toggles. | Read/Write
PINTLK | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset (enables HMI button). | Read Only
PINTLK | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset latched interlocks. | Read/Write
PINTLK | Val_BankMap | DINT | 0 | Decimal | Map of interlock banks detected. | Read Only
PINTLK | Val_BankSts | DINT | 0 | Decimal | Map of interlock banks statuses. | Read Only
PLLS | Sts_eNotify | SINT | 0 | Decimal | Current alarm level and acknowledgement (enumeration). | Read Only
PLLS | Sts_eNotifyCantStart | SINT | 0 | Decimal | Current alarm level and acknowledgement (enumeration). | Read Only
PLLS | Sts_eNotifyCantStop | SINT | 0 | Decimal | Current alarm level and acknowledgement (enumeration). | Read Only
PLLS | CmdSrc | P_COMMAND_SOURCE | {...} |  | Control / command source selection. | Read/Write
PLLS | Val_RankList | SINT[32] | {...} | Decimal | Rank list of motor numbers: [0] = lead, [1] = lag, etc... | Read Only
PLLS | Sts_bStsList | SINT[32] | {...} | Decimal | Rank list of motor status: [0]=lead, [1]=lag, etc.; .0 = Avaiable, .1 = Stopped, .2 = Starting, .3 = Running, .4 = Stopping, .5 = Out of Service (Maint). | Read Only
PLLS | Val_PrefList | SINT[32] | {...} | Decimal | Rank list of motor preferences: [0] = lead, [1] = lag, etc... | Read Only
PLLS | Val_UsrList | INT[32] | {...} | Decimal | Rank list of user sort criteria: [0] = lead, [1] = lag, etc... | Read Only
PLLS | Val_PrioList | SINT[32] | {...} | Decimal | Rank list of motor priorities: [0] = lead, [1] = lag, etc... | Read Only
PLLS | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to reset all alarms and latched shed conditions. | Read/Write
PLLS | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms requiring reset. | Read/Write
PLLS | OCmd_Rotate | BOOL | 0 | Decimal | Operator command to rotate assignments (cycle lead to end of list). | Read/Write
PLLS | OCmd_Stop | BOOL | 0 | Decimal | Operator command to stop motor group. | Read/Write
PLLS | OCmd_Start | BOOL | 0 | Decimal | Operator command to start motor group. | Read/Write
PLLS | MCmd_Check | BOOL | 0 | Decimal | Maintenance command to check (not bypass) all interlocks and permissives. | Read/Write
PLLS | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance command to bypass all bypassable interlocks and permissives. | Read/Write
PLLS | MSet_MotorOoS | DINT | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | Set bits indicate which motors have been taken out of service by maintenance. | Read/Write
PLLS | OSet_Demand | DINT | 0 | Decimal | Operator setting for number of motors to run (MinDemand.. MaxDemand). Valid = Cfg_MinDemand <= OSet_Damand <= Cfg_MaxDemand. | Read/Write
PLLS | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll (enables HMI button). | Read Only
PLLS | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset (enables HMI button). | Read Only
PLLS | ORdy_Demand | BOOL | 0 | Decimal | 1 = Ready for OSet_Demand (enables numeric entry). | Read Only
PLLS | ORdy_Rotate | BOOL | 0 | Decimal | 1 = Ready for OCmd_Rotate (enables HMI button). | Read Only
PLLS | ORdy_Stop | BOOL | 0 | Decimal | 1 = Ready for OCmd_Stop (enables HMI button). | Read Only
PLLS | ORdy_Start | BOOL | 0 | Decimal | 1 = Ready for OCmd_Start (enables HMI button). | Read Only
PLLS | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready for MCmd_Check (enables HMI button). | Read Only
PLLS | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready for MCmd_Bypass (enables HMI button). | Read Only
PLLS | Sts_eNotifyIntlkTrip | SINT | 0 | Decimal | Current alarm level and acknowledgement (enumeration). | Read Only
PLLS | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
PLLS | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
PLLS | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
PLLS | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
PLLS | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
PLLS | OCmd_Unlock | BOOL | 0 | Decimal | Operator command to unlock / release (allow Program to acquire) ownership. The instruction clears this operand automatically. | Read/Write
PLLS | OCmd_Prog | BOOL | 0 | Decimal | Operator command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write
PLLS | OCmd_Oper | BOOL | 0 | Decimal | Operator command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write
PLLS | OCmd_Normal | BOOL | 0 | Decimal | Operator command to select Normal (Operator or Program). The instruction clears this operand automatically. | Read/Write
PLLS | OCmd_Lock | BOOL | 0 | Decimal | Operator command to lock Operator (disallow Program). The instruction clears this operand automatically. | Read/Write
PLLS | OCmd_CmdCncl | BOOL | 0 | Decimal | Operator command to cancel command request. The instruction clears this operand automatically. | Read/Write
PLLS | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
PLLS | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
PLLS | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
PLLS | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
PLLS | MCmd_Rel | BOOL | 0 | Decimal | Maintenance command to release ownership (Maintenance to Operator/Program/External/Override). The instruction clears this operand automatically. | Read/Write
PLLS | MCmd_OoS | BOOL | 0 | Decimal | Maintenance command to select Out of Service. The instruction clears this operand automatically. | Read/Write
PLLS | MCmd_IS | BOOL | 0 | Decimal | Maintenance command to select In Service. The instruction clears this operand automatically. | Read/Write
PLLS | MCmd_Acq | BOOL | 0 | Decimal | Maintenance command to acquire ownership (Operator/Program/External/Override to Maintenance). The instruction clears this operand automatically. | Read/Write
PLLS | OCmd_SetPrefs | BOOL | 0 | Decimal | Operator command to set motor preferences. | Read/Write
PLLS | OCmd_ResetPrefs | BOOL | 0 | Decimal | Operator command to reset all motor preferences to 0. | Read/Write
PLLS | HMI_BusObjIndex | DINT | 0 | Decimal | HMI bus object index. | Read Only
PMTR | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
PMTR | ORdy_Stop | BOOL | 0 | Decimal | 1 = Ready for OCmd_Stop, enable HMI button. | Read Only
PMTR | ORdy_Start2 | BOOL | 0 | Decimal | 1 = Ready for OCmd_Start2, enable HMI button. | Read Only
PMTR | ORdy_Start1 | BOOL | 0 | Decimal | 1 = Ready for OCmd_Start1, enable HMI button. | Read Only
PMTR | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = A latched alarm or shed condition is ready to be reset or acknowledged. | Read Only
PMTR | ORdy_Reset | BOOL | 0 | Decimal | 1 = A latched alarm or shed condition is ready to be reset. | Read Only
PMTR | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
PMTR | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
PMTR | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
PMTR | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
PMTR | OCmd_Stop | BOOL | 0 | Decimal | Operator command to Stop Motor. The instruction clears this operand automatically. | Read/Write
PMTR | OCmd_Start2 | BOOL | 0 | Decimal | Operator command to Start Motor Reverse / Fast. The instruction clears this operand automatically. | Read/Write
PMTR | OCmd_Start1 | BOOL | 0 | Decimal | Operator command to Start Motor Forward / Slow. The instruction clears this operand automatically. | Read/Write
PMTR | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to acknowledge and reset all alarms and latched shed conditions. The use of OCmd_ResetAckAll is restricted to HMI. The instruction clears this operand automatically. | Read/Write
PMTR | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write
PMTR | OCmd_Prog | BOOL | 0 | Decimal | Operator command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write
PMTR | OCmd_Oper | BOOL | 0 | Decimal | Operator command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write
PMTR | OCmd_Normal | BOOL | 0 | Decimal | Operator command to select Normal (Operator or Program). The instruction clears this operand automatically. | Read/Write
PMTR | OCmd_Lock | BOOL | 0 | Decimal | Operator command to lock Operator (disallow Program). The instruction clears this operand automatically. | Read/Write
PMTR | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
PMTR | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
PMTR | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
PMTR | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready for MCmd_Check, enable HMI button. | Read Only
PMTR | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready for MCmd_Bypass, enable HMI button. | Read Only
PMTR | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
PMTR | MCmd_OoS | BOOL | 0 | Decimal | Maintenance command to select Out of service. The instruction clears this operand automatically. | Read/Write
PMTR | MCmd_IS | BOOL | 0 | Decimal | Maintenance command to select In service. The instruction clears this operand automatically. | Read/Write
PMTR | MCmd_Check | BOOL | 0 | Decimal | Maintenance command to check (not bypass) all interlocks and permissives. The instruction clears this operand automatically. | Read/Write
PMTR | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance command to bypass all bypassable interlocks and permissives. The instruction clears this operand automatically. | Read/Write
PMTR | MCmd_Acq | BOOL | 0 | Decimal | Maintenance command to acquire ownership (Operator/Program/External/Override to Maintenance). The instruction clears this operand automatically. | Read/Write
PMTR | CmdSrc | P_COMMAND_SOURCE | {...} |  | Command Source | Read/Write
PMTR | ORdy_Jog2 | BOOL | 0 | Decimal | 1 = Ready for OCmd_Jog2, enable HMI button. | Read Only
PMTR | ORdy_Jog1 | BOOL | 0 | Decimal | 1 = Ready for OCmd_Jog1, enable HMI button. | Read Only
PMTR | OCmd_Jog2 | BOOL | 0 | Decimal | Operator command to Jog Motor Reverse / Fast. The instruction clears this operand automatically if max jog time is reached. | Read/Write
PMTR | OCmd_Jog1 | BOOL | 0 | Decimal | Operator command to Jog Motor Forward / Slow. The instruction clears this operand automatically if max jog time is reached. | Read/Write
PMTR | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
PMTR | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
PMTR | MCmd_Physical | BOOL | 0 | Decimal | Maintenance command to select Physical device operation (not simulated). The instruction clears this operand automatically. | Read/Write
PMTR | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance command to select Virtual (simulated) device operation. The instruction clears this operand automatically. | Read/Write
PMTR | Sts_FaultDesc | STRING | '' |  | Description of intelligent motor controller fault, lookup from last fault code. | Read Only
PMTR | HMI_BusObjIndex | DINT | 0 | Decimal | This object$'s index in the bus array, for use by HMI display. | Read Only
PMTR | MCmd_Rel | BOOL | 0 | Decimal | Maintenance command to release ownership (Maintenance to Operator/Program/External/Override). The instruction clears this operand automatically. | Read/Write
PMTR | OCmd_Unlock | BOOL | 0 | Decimal | Operator command to unlock / release (allow Program to acquire) ownership. The instruction clears this operand automatically. | Read/Write
PNPOS | Wrk_bInp | DINT | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | Buffer for device position feedback input bits, bit .1 thru .30. | Read/Write
PNPOS | OSet_Pos | SINT | 0 | Decimal | Operator Setting of commanded position 1 to 30, 0 = No command. The instruction clears this operand automatically. | Read/Write
PNPOS | HMI_eCmdPos | SINT | 0 | Decimal | Last commanded position: 0 = None, 1 = Position 1, 2 = Position 2, ..., 30 = Position 30. | Read Only
PNPOS | CmdSrc | P_COMMAND_SOURCE | {...} |  | Command source selection. | Read/Write
PNPOS | Wrk_bOut | DINT | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | Buffer for position request output bits, bit .1 thru .30. | Read Only
PNPOS | HMI_BusObjIndex | DINT | 0 | Decimal | This object$'s index in the bus array, for use by HMI display. | Read Only
PNPOS | OCmd_Unlock | BOOL | 0 | Decimal | Operator Command to unlock Operator command source and allow Program to acquire. The instruction clears this operand automatically. | Read/Write
PNPOS | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator Command to acknowledge all alarms and reset latched alarms and shed conditions. The instruction clears this operand automatically. | Read/Write
PNPOS | OCmd_Reset | BOOL | 0 | Decimal | Operator Command to reset shed latches and returned-to-normal latched alarms. The instruction clears this operand automatically. | Read/Write
PNPOS | OCmd_Prog | BOOL | 0 | Decimal | Operator Command to select Program (unlocked) command source. The instruction clears this operand automatically. | Read/Write
PNPOS | OCmd_Oper | BOOL | 0 | Decimal | Operator Command to select Operator (unlocked) command source. The instruction clears this operand automatically. | Read/Write
PNPOS | OCmd_Normal | BOOL | 0 | Decimal | Operator Command to select configured normal command source (Operator or Program). The instruction clears this operand automatically. | Read/Write
PNPOS | OCmd_Lock | BOOL | 0 | Decimal | Operator Command to select Operator Locked command source and disallow Program. The instruction clears this operand automatically. | Read/Write
PNPOS | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
PNPOS | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
PNPOS | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
PNPOS | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
PNPOS | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
PNPOS | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready for MCmd_Check, enable HMI button. | Read Only
PNPOS | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready for MCmd_Bypass, enable HMI button. | Read Only
PNPOS | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
PNPOS | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance Command to select Virtual device operation. The instruction clears this operand automatically. | Read/Write
PNPOS | MCmd_Rel | BOOL | 0 | Decimal | Maintenance Command to release Maintenance command source. The instruction clears this operand automatically. | Read/Write
PNPOS | MCmd_Physical | BOOL | 0 | Decimal | Maintenance Command to select Physical device operation. The instruction clears this operand automatically. | Read/Write
PNPOS | MCmd_OoS | BOOL | 0 | Decimal | Maintenance Command to select Out of Service. The instruction clears this operand automatically. | Read/Write
PNPOS | MCmd_IS | BOOL | 0 | Decimal | Maintenance Command to select In Service. The instruction clears this operand automatically. | Read/Write
PNPOS | MCmd_Check | BOOL | 0 | Decimal | Maintenance Command to remove bypass and check all interlocks and permissives. The instruction clears this operand automatically. | Read/Write
PNPOS | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance Command to bypass all bypassable interlocks and permissives. The instruction clears this operand automatically. | Read/Write
PNPOS | MCmd_Acq | BOOL | 0 | Decimal | Maintenance Command to acquire Maintenance command source. The instruction clears this operand automatically. | Read/Write
PNPOS | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
PNPOS | ORdy_Pos | BOOL | 0 | Decimal | 1 = Ready for OSet_Pos, enable HMI data entry field or command buttons. | Read Only
PNPOS | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll, enable HMI button. | Read Only
PNPOS | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only
PNPOS | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
PNPOS | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
PNPOS | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
PNPOS | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
PPERM | Wrk_Inp | DINT | 2#1111_1111_1111_1111_1111_1111_1111_1111 | Binary | Collection copy of Inp_PermXXs. | Read/Write
PPERM | MSet_Bypass | DINT | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | Individual condition maintenance bypass toggles. | Read/Write
PPID | HMI_BusObjIndex | DINT | 0 | Decimal | HMI bus object index. | Read Only
PPID | OCmd_SPRampStart | BOOL | 0 | Decimal | Operator command to initiate SP ramping. The instruction clears this operand automatically. | Read/Write
PPID | OCmd_SPRampStop | BOOL | 0 | Decimal | Operator command to stop SP ramping. The instruction clears this operand automatically. | Read/Write
PPID | OSet_Ratio | REAL | 1 | Float | Operator setting for Ratio, loop mode Cascade/Ratio and Ratio enabled (unitless). Valid = 0.0 to maximum positive float. | Read/Write
PPID | OSet_SP | REAL | 0 | Float | Operator setting for Setpoint, loop mode Auto (PVEU). Valid any float. | Read/Write
PPID | OSet_SPTarget | REAL | 0 | Float | Operator setting for Setpoint ramp target, endpoint for ramp wizard (PVEU). Valid any float. | Read/Write
PPID | OSet_SPRampTime | REAL | 0 | Float | Operator setting for Setpoint ramp time, time to reach target for ramp wizard (seconds). Valid = 0.0 to 28800.0 seconds. | Read/Write
PPID | OSet_CV | REAL | 0 | Float | Operator setting for CV, loop mode Manual (CVEU). Valid any float. | Read/Write
PPID | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance command to bypass all bypassable interlocks. The instruction clears this operand automatically. | Read/Write
PPID | MCmd_Check | BOOL | 0 | Decimal | Maintenance command to check, not bypass, all interlocks. The instruction clears this operand automatically. | Read/Write
PPID | MCmd_OoS | BOOL | 0 | Decimal | Maintenance command to select Out of Service. The instruction clears this operand automatically. | Read/Write
PPID | MCmd_IS | BOOL | 0 | Decimal | Maintenance command to select In Service. The instruction clears this operand automatically. | Read/Write
PPID | MCmd_Acq | BOOL | 0 | Decimal | Maintenance command to acquire ownership (Operator/Program/External/Override to Maintenance). The instruction clears this operand automatically. | Read/Write
PPID | MCmd_Rel | BOOL | 0 | Decimal | Maintenance command to release ownership (Maintenance to Operator/Program/External/Override). The instruction clears this operand automatically. | Read/Write
PPID | OCmd_Oper | BOOL | 0 | Decimal | Operator command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write
PPID | OCmd_Prog | BOOL | 0 | Decimal | Operator command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write
PPID | OCmd_Lock | BOOL | 0 | Decimal | Operator command to lock Operator (disallow Program). The instruction clears this operand automatically. | Read/Write
PPID | OCmd_Unlock | BOOL | 0 | Decimal | Operator command to unlock or release (allow Program to acquire) ownership. The instruction clears this operand automatically. | Read/Write
PPID | OCmd_Normal | BOOL | 0 | Decimal | Operator command to select Normal (Operator or Program). The instruction clears this operand automatically. | Read/Write
PPID | OCmd_Auto | BOOL | 0 | Decimal | Operator command to select Automatic loop mode. The instruction clears this operand automatically. | Read/Write
PPID | OCmd_Casc | BOOL | 0 | Decimal | Operator command to select Cascade/Ratio loop mode. The instruction clears this operand automatically. | Read/Write
PPID | OCmd_Man | BOOL | 0 | Decimal | Operator command to select Manual loop mode. The instruction clears this operand automatically. | Read/Write
PPID | OCmd_NormLM | BOOL | 0 | Decimal | Operator command to select loop mode configured as Normal (see Cfg_NormLM). The instruction clears this operand automatically. | Read/Write
PPID | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write
PPID | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to acknowledge and reset all alarms and latched shed conditions. The use of OCmd_ResetAckAll is restricted to HMI. The instruction clears this operand automatically. | Read/Write
PPID | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready for MCmd_Bypass, enable HMI button. | Read Only
PPID | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready for MCmd_Check, enable HMI button. | Read Only
PPID | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
PPID | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
PPID | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
PPID | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
PPID | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
PPID | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
PPID | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
PPID | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
PPID | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
PPID | ORdy_Auto | BOOL | 0 | Decimal | 1 = Ready for OCmd_Auto, enables HMI button. | Read Only
PPID | ORdy_Casc | BOOL | 0 | Decimal | 1 = Ready for OCmd_Casc, enables HMI button. | Read Only
PPID | ORdy_CV | BOOL | 0 | Decimal | 1 = Ready for OSet_CV, enables data entry field. | Read Only
PPID | ORdy_Man | BOOL | 0 | Decimal | 1 = Ready for OCmd_Man, enables HMI button. | Read Only
PPID | ORdy_NormLM | BOOL | 0 | Decimal | 1 = Ready for OCmd_NormLM, enables HMI button. | Read Only
PPID | ORdy_Ratio | BOOL | 0 | Decimal | 1 = Ready for OSet_Ratio, enables data entry field. | Read Only
PPID | ORdy_SP | BOOL | 0 | Decimal | 1 = Ready for OSet_SP, enables data entry field. | Read Only
PPID | ORdy_SPRampStart | BOOL | 0 | Decimal | 1 = Ready for OCmd_SPRampStart, enables HMI button. | Read Only
PPID | ORdy_SPRampStop | BOOL | 0 | Decimal | 1 = Ready for OCmd_SPRampStop, enables HMI button. | Read Only
PPID | ORdy_SPTarget | BOOL | 0 | Decimal | 1 = Ready for OSet_SPTarget, enables data entry field. | Read Only
PPID | ORdy_SPRampTime | BOOL | 0 | Decimal | 1 = Ready for OSet_SPRampTime, enables data entry field. | Read Only
PPID | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enables HMI button. | Read Only
PPID | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = At least one alarm or latched shed condition requires Reset or Acknowledgement. | Read Only
PPID | CmdSrc | P_COMMAND_SOURCE | {...} |  | Command Source. | Read/Write
PRT | MCmd_ClearTotHrs | BOOL | 0 | Decimal | Maintenance command to clear total running time | Read/Write
PRT | MCmd_ClearMaxHrs | BOOL | 0 | Decimal | Maintenance command to clear maximum (continuous) run time for any start | Read/Write
PRT | MCmd_ClearStarts | BOOL | 0 | Decimal | Maintenance command to clear count of starts (attempts) | Read/Write
PVLV | CmdSrc | P_COMMAND_SOURCE | {...} |  | Command Source | Read/Write
PVLV | OCmd_Stop | BOOL | 0 | Decimal | Operator command to stop valve motion. The instruction clears this operand automatically. | Read/Write
PVLV | OCmd_Trip | BOOL | 0 | Decimal | Operator command to trip valve. | Read/Write
PVLV | MCmd_Check | BOOL | 0 | Decimal | Maintenance command to check (not bypass) all interlocks. The instruction clears this operand automatically. | Read/Write
PVLV | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance command to bypass all bypassable interlocks. The instruction clears this operand automatically. | Read/Write
PVLV | OCmd_Pos1 | BOOL | 0 | Decimal | Operator command to move valve to Position 1. The instruction clears this operand automatically. | Read/Write
PVLV | OCmd_Pos1Pulse | BOOL | 0 | Decimal | Operator command to pulse valve that is in Position 2, to Position 1 once. The instruction clears this operand automatically. | Read/Write
PVLV | OCmd_ContPulse | BOOL | 0 | Decimal | Operator command to pulse valve continuously. The instruction clears this operand automatically. | Read/Write
PVLV | OCmd_Pos2 | BOOL | 0 | Decimal | Operator command to move valve to Position 2. The instruction clears this operand automatically. | Read/Write
PVLV | OCmd_Pos2Pulse | BOOL | 0 | Decimal | Operator command to pulse valve that is in Position 1, to Position 2 once. The instruction clears this operand automatically. | Read/Write
PVLV | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms requiring reset. The instruction clears this operand automatically. | Read/Write
PVLV | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to reset all alarms and latched shed conditions. The use of OCmd_ResetAckAll is restricted to HMI. The instruction clears this operand automatically. | Read/Write
PVLV | ORdy_Pos1 | BOOL | 0 | Decimal | 1 = Ready to receive OCmd_Pos1, enable HMI button. | Read Only
PVLV | ORdy_Pos1Pulse | BOOL | 0 | Decimal | 1 = Ready to receive OCmd_Pos1pulse, enable HMI button. | Read Only
PVLV | ORdy_ContPulse | BOOL | 0 | Decimal | 1 = Ready to receive OCmd_Contpulse, enable HMI button. | Read Only
PVLV | ORdy_Pos2 | BOOL | 0 | Decimal | 1 = Ready to receive OCmd_Pos2, enable HMI button. | Read Only
PVLV | ORdy_Pos2Pulse | BOOL | 0 | Decimal | 1 = Ready to receive OCmd_Pos2pulse, enable HMI button. | Read Only
PVLV | ORdy_Reset | BOOL | 0 | Decimal | 1 = At least one alarm or shed condition requires reset. | Read Only
PVLV | ORdy_Trip | BOOL | 0 | Decimal | 1 = Ready for OCmd_trip (enables HMI button). | Read Only
PVLV | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready to receive OCmd_Bypass, enable HMI button. | Read Only
PVLV | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready to receive OCmd_Check, enable HMI button. | Read Only
PVLV | MCmd_Acq | BOOL | 0 | Decimal | Maintenance command to acquire ownership (Operator/Program/External/Override to Maintenance). The instruction clears this operand automatically. | Read/Write
PVLV | MCmd_IS | BOOL | 0 | Decimal | Maintenance command to select in service. The instruction clears this operand automatically. | Read/Write
PVLV | MCmd_OoS | BOOL | 0 | Decimal | Maintenance command to select out of service. The instruction clears this operand automatically. | Read/Write
PVLV | MCmd_Rel | BOOL | 0 | Decimal | Maintenance command to release ownership (Maintenance to Operator/Program/External/Override). The instruction clears this operand automatically. | Read/Write
PVLV | OCmd_Lock | BOOL | 0 | Decimal | Operator command to lock Operator (disallow Program). The instruction clears this operand automatically. | Read/Write
PVLV | OCmd_Normal | BOOL | 0 | Decimal | Operator command to select normal (Operator or Program). The instruction clears this operand automatically. | Read/Write
PVLV | OCmd_Oper | BOOL | 0 | Decimal | Operator command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write
PVLV | OCmd_Prog | BOOL | 0 | Decimal | Operator command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write
PVLV | OCmd_Unlock | BOOL | 0 | Decimal | Operator command to unlock / release (allow Program to acquire) ownership. The instruction clears this operand automatically. | Read/Write
PVLV | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
PVLV | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
PVLV | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
PVLV | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
PVLV | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
PVLV | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
PVLV | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
PVLV | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
PVLV | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
PVLV | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
PVLV | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
PVLV | MCmd_Physical | BOOL | 0 | Decimal | Maintenance Command to select Physical device operation (not simulated) | Read/Write
PVLV | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance Command to select Virtual (simulated) device operation | Read/Write
PVLV | HMI_BusObjIndex | DINT | 0 | Decimal | HMI bus object index | Read/Write
PVLV | XRdy_ContPulse | BOOL | 0 | Decimal | 1 = Ready to receive XCmd_Contpulse, enable HMI button. | Read Only
PVLV | XRdy_Lock | BOOL | 0 | Decimal | 1 = Ready for XCmd_Lock, enable HMI button. | Read Only
PVLV | XRdy_Normal | BOOL | 0 | Decimal | 1 = Ready for XCmd_Normal, enable HMI button. | Read Only
PVLV | XRdy_Oper | BOOL | 0 | Decimal | 1 = Ready for XCmd_Oper, enable HMI button. | Read Only
PVLV | XRdy_Pos1 | BOOL | 0 | Decimal | 1 = Ready to receive XCmd_Pos1, enable HMI button. | Read Only
PVLV | XRdy_Pos1Pulse | BOOL | 0 | Decimal | 1 = Ready to receive XCmd_Pos1pulse, enable HMI button. | Read Only
PVLV | XRdy_Pos2 | BOOL | 0 | Decimal | 1 = Ready to receive XCmd_Pos2, enable HMI button. | Read Only
PVLV | XRdy_Pos2Pulse | BOOL | 0 | Decimal | 1 = Ready to receive XCmd_Pos2pulse, enable HMI button. | Read Only
PVLV | XRdy_Prog | BOOL | 0 | Decimal | 1 = Ready for XCmd_Prog, enable HMI button. | Read Only
PVLV | XRdy_Trip | BOOL | 0 | Decimal | 1 = Ready for XCmd_Trip (enables HMI button). | Read Only
PVLV | XRdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for XCmd_Unlock, enable HMI button. | Read Only
PVLV | ORdy_Stop | BOOL | 0 | Decimal | 1 = Ready for OCmd_Stop (enables HMI button). | Read Only
PVLV | XRdy_Stop | BOOL | 0 | Decimal | 1 = Ready for XCmd_Stop (enables HMI button). | Read Only
PVLV | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = At least one alarm or latched shed condition requires reset or acknowledgement. | Read Only
PVLV | Wrk_NrdyTrip | BOOL | 0 | Decimal | 1 = Valve not ready: tripped (at object or by command). | Read Only
PVLV | Wrk_NrdyIOFault | BOOL | 0 | Decimal | 1 = Valve is not ready: IOFault (shed requires reset). | Read Only
PVLV | Wrk_NrdyActuatorFault | BOOL | 0 | Decimal | 1 = Valve not ready:actuator fault (fault or shed requires reset). | Read Only
PVLV | Wrk_IntlkTrip | BOOL | 0 | Decimal | 1 = Valve tripped by an interlock not ok. | Read Only
PVLV | Wrk_NrdyFail | BOOL | 0 | Decimal | 1 = Valve is not ready: object failure (shed requires reset). | Read Only
PVLVMP | HMI_eCmdState | SINT | 0 | Decimal | Command to valve, for use on HMI/dialog: 0 = None, 1 = Close, 3 = Open, 4 = Lift lower seat, 5 = Lift upper seat, 6 = Clean cavity, 8 = Clean lower seat, 10 = Clean upper seat. | Read Only
PVLVMP | CmdSrc | P_COMMAND_SOURCE | {...} |  | Command source selection. | Read/Write
PVLVMP | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll, enable HMI button. | Read Only
PVLVMP | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only
PVLVMP | ORdy_CleanUpper | BOOL | 0 | Decimal | 1 = Ready for OCmd_CleanUpper, enables HMI button. | Read Only
PVLVMP | ORdy_CleanLower | BOOL | 0 | Decimal | 1 = Ready for OCmd_CleanLower, enable HMI button. | Read Only
PVLVMP | ORdy_CleanCavity | BOOL | 0 | Decimal | 1 = Ready for OCmd_CleanCavity, enable HMI button. | Read Only
PVLVMP | ORdy_LiftUpper | BOOL | 0 | Decimal | 1 = Ready for OCmd_LiftUpper, enable HMI button. | Read Only
PVLVMP | ORdy_LiftLower | BOOL | 0 | Decimal | 1 = Ready for OCmd_LiftLower, enable HMI button. | Read Only
PVLVMP | ORdy_Open | BOOL | 0 | Decimal | 1 = Ready for OCmd_Open, enable HMI button. | Read Only
PVLVMP | ORdy_Close | BOOL | 0 | Decimal | 1 = Ready for OCmd_Close, enable HMI button. | Read Only
PVLVMP | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator Command to acknowledge all alarms and reset latched alarms and shed conditions. The instruction clears this operand automatically. | Read/Write
PVLVMP | OCmd_Reset | BOOL | 0 | Decimal | Operator Command to reset shed latches and returned-to-normal latched alarms. The instruction clears this operand automatically. | Read/Write
PVLVMP | OCmd_CleanUpper | BOOL | 0 | Decimal | Operator Command to clean valve upper seat. The instruction clears this operand automatically. | Read/Write
PVLVMP | OCmd_CleanLower | BOOL | 0 | Decimal | Operator Command to clean valve lower seat. The instruction clears this operand automatically. | Read/Write
PVLVMP | OCmd_CleanCavity | BOOL | 0 | Decimal | Operator Command to clean valve leakage cavity. The instruction clears this operand automatically. | Read/Write
PVLVMP | OCmd_LiftUpper | BOOL | 0 | Decimal | Operator Command to lift upper valve seat. The instruction clears this operand automatically. | Read/Write
PVLVMP | OCmd_LiftLower | BOOL | 0 | Decimal | Operator Command to lift lower valve seat. The instruction clears this operand automatically. | Read/Write
PVLVMP | OCmd_Open | BOOL | 0 | Decimal | Operator Command to open valve. The instruction clears this operand automatically. | Read/Write
PVLVMP | OCmd_Close | BOOL | 0 | Decimal | Operator Command to close valve. The instruction clears this operand automatically. | Read/Write
PVLVMP | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
PVLVMP | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
PVLVMP | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
PVLVMP | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
PVLVMP | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
PVLVMP | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready for MCmd_Check, enable HMI button. | Read Only
PVLVMP | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready for MCmd_Bypass, enable HMI button. | Read Only
PVLVMP | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
PVLVMP | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance Command to select Virtual device operation. The instruction clears this operand automatically. | Read/Write
PVLVMP | MCmd_Rel | BOOL | 0 | Decimal | Maintenance Command to release Maintenance command source. The instruction clears this operand automatically. | Read/Write
PVLVMP | MCmd_Physical | BOOL | 0 | Decimal | Maintenance Command to select Physical device operation. The instruction clears this operand automatically. | Read/Write
PVLVMP | MCmd_OoS | BOOL | 0 | Decimal | Maintenance Command to select Out of Service. The instruction clears this operand automatically. | Read/Write
PVLVMP | MCmd_IS | BOOL | 0 | Decimal | Maintenance Command to select In Service. The instruction clears this operand automatically. | Read/Write
PVLVMP | MCmd_Check | BOOL | 0 | Decimal | Maintenance Command to remove bypass and check all interlocks and permissives. The instruction clears this operand automatically. | Read/Write
PVLVMP | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance Command to bypass all bypassable interlocks and permissives. The instruction clears this operand automatically. | Read/Write
PVLVMP | MCmd_Acq | BOOL | 0 | Decimal | Maintenance Command to acquire Maintenance command source. The instruction clears this operand automatically. | Read/Write
PVLVMP | HMI_BusObjIndex | DINT | 0 | Decimal | This object$'s index in the bus array, for use by HMI display. | Read Only
PVLVMP | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
PVLVMP | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
PVLVMP | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
PVLVMP | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
PVLVMP | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
PVLVMP | OCmd_Unlock | BOOL | 0 | Decimal | Operator Command to unlock Operator command source and allow Program to acquire. The instruction clears this operand automatically. | Read/Write
PVLVMP | OCmd_Prog | BOOL | 0 | Decimal | Operator Command to select Program (unlocked) command source. The instruction clears this operand automatically. | Read/Write
PVLVMP | OCmd_Oper | BOOL | 0 | Decimal | Operator Command to select Operator (unlocked) command source. The instruction clears this operand automatically. | Read/Write
PVLVMP | OCmd_Normal | BOOL | 0 | Decimal | Operator Command to select configured normal command source (Operator or Program). The instruction clears this operand automatically. | Read/Write
PVLVMP | OCmd_Lock | BOOL | 0 | Decimal | Operator Command to select Operator Locked command source and disallow Program. The instruction clears this operand automatically. | Read/Write
PVLVMP | MCmd_ToggleLocator | BOOL | 0 | Decimal | Maintenance Command to toggle on/off valve locator/beacon. | Read/Write
PVLVMP | MRdy_ToggleLocator | BOOL | 0 | Decimal | 1 = Ready for MCmd_ToggleLocator, enable HMI button. | Read Only
PVLVS | MCmd_ClearMAvgs | BOOL | 0 | Decimal | Maintenance command to clear moving average stroke times. | Read/Write
PVLVS | MCmd_ClearSlowCounts | BOOL | 0 | Decimal | Maintenance command to clear device slow count statistics. | Read/Write
PVLVS | MCmd_ClearStrokeCounts | BOOL | 0 | Decimal | Maintenance command to clear stroke count statistics. | Read/Write
PVLVS | MCmd_ClearMaxTimes | BOOL | 0 | Decimal | Maintenance command to clear maximum time statistics. | Read/Write
PVLVS | MCmd_ClearTotTimes | BOOL | 0 | Decimal | Maintenance command to clear total time statistics. | Read/Write
PVSD | Wrk_StopT | TIMER | {...} |  | Stop Check Timer for Fail to Stop. | Read Only
PVSD | Wrk_StartT | TIMER | {...} |  | Start Check Timer for Fail to Start. | Read Only
PVSD | OSet_SpeedRef | REAL | 0 | Float | Operator Setting of Speed Reference, in speed reference engineering units. Valid = any float (will be clamped at configured Min and Max). | Read/Write
PVSD | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
PVSD | ORdy_Stop | BOOL | 0 | Decimal | 1 = Ready for OCmd_Stop, enable HMI button. | Read Only
PVSD | ORdy_StartRev | BOOL | 0 | Decimal | 1 = Ready for OCmd_StartRev, enable HMI button. | Read Only
PVSD | ORdy_StartFwd | BOOL | 0 | Decimal | 1 = Ready for OCmd_StartFwd, enable HMI button. | Read Only
PVSD | ORdy_SpeedRef | BOOL | 0 | Decimal | 1 = Ready for OSet_SpeedRef, enable data entry field. | Read Only
PVSD | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = A latched alarm or shed condition is ready to be reset or acknowledged. | Read Only
PVSD | ORdy_Reset | BOOL | 0 | Decimal | 1 = A latched alarm or shed condition is ready to be reset. | Read Only
PVSD | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
PVSD | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
PVSD | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
PVSD | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
PVSD | OCmd_Stop | BOOL | 0 | Decimal | Operator command to Stop Drive. The instruction clears this operand automatically. | Read/Write
PVSD | OCmd_StartRev | BOOL | 0 | Decimal | Operator command to Start Drive Reverse. The instruction clears this operand automatically. | Read/Write
PVSD | OCmd_StartFwd | BOOL | 0 | Decimal | Operator command to Start Drive Forward. The instruction clears this operand automatically. | Read/Write
PVSD | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to acknowledge and reset all alarms and latched shed conditions. The use of OCmd_ResetAckAll is restricted to HMI. The instruction clears this operand automatically. | Read/Write
PVSD | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write
PVSD | OCmd_Prog | BOOL | 0 | Decimal | Operator command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write
PVSD | OCmd_Oper | BOOL | 0 | Decimal | Operator command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write
PVSD | OCmd_Normal | BOOL | 0 | Decimal | Operator command to select Normal (Operator or Program). The instruction clears this operand automatically. | Read/Write
PVSD | OCmd_Lock | BOOL | 0 | Decimal | Operator command to lock Operator (disallow Program). The instruction clears this operand automatically. | Read/Write
PVSD | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
PVSD | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
PVSD | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
PVSD | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready for MCmd_Check, enable HMI button. | Read Only
PVSD | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready for MCmd_Bypass, enable HMI button. | Read Only
PVSD | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
PVSD | MCmd_OoS | BOOL | 0 | Decimal | Maintenance command to select Out of Service. The instruction clears this operand automatically. | Read/Write
PVSD | MCmd_IS | BOOL | 0 | Decimal | Maintenance command to select In Service. The instruction clears this operand automatically. | Read/Write
PVSD | MCmd_Check | BOOL | 0 | Decimal | Maintenance command to check (not bypass) all interlocks and permissives. The instruction clears this operand automatically. | Read/Write
PVSD | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance command to bypass all bypassable interlocks and permissives. The instruction clears this operand automatically. | Read/Write
PVSD | MCmd_Acq | BOOL | 0 | Decimal | Maintenance command to acquire ownership (Operator/Program/External/Override to Maintenance). The instruction clears this operand automatically. | Read/Write
PVSD | CmdSrc | P_COMMAND_SOURCE | {...} |  | Command Source | Read/Write
PVSD | ORdy_OutDatalink | BOOL | 0 | Decimal | 1 = Ready for OSet_OutDatalink, enable data entry field. | Read Only
PVSD | OSet_OutDatalink | REAL | 0 | Float | Operator Setting of Output Datalink, in output datalink engineering units. Valid = any float (will be clamped at configured Min and Max). | Read/Write
PVSD | ORdy_JogRev | BOOL | 0 | Decimal | 1 = Ready for OCmd_JogRev, enable HMI button. | Read Only
PVSD | ORdy_JogFwd | BOOL | 0 | Decimal | 1 = Ready for OCmd_JogFwd, enable HMI button. | Read Only
PVSD | OCmd_JogRev | BOOL | 0 | Decimal | Operator command to Jog Drive Reverse. The instruction clears this operand automatically if max jog time is reached. | Read/Write
PVSD | OCmd_JogFwd | BOOL | 0 | Decimal | Operator command to Jog Drive Forward. The instruction clears this operand automatically if max jog time is reached. | Read/Write
PVSD | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
PVSD | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
PVSD | MCmd_Physical | BOOL | 0 | Decimal | Maintenance command to select Physical device operation (not simulated). The instruction clears this operand automatically. | Read/Write
PVSD | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance command to select Virtual (simulated) device operation. The instruction clears this operand automatically. | Read/Write
PVSD | HMI_BusObjIndex | DINT | 0 | Decimal | This object$'s index in the bus array, for use by HMI display. | Read Only
PVSD | Sts_FaultDesc | STRING | '' |  | Description of motor controller fault, lookup from last fault code. | Read Only
PVSD | MCmd_Rel | BOOL | 0 | Decimal | Maintenance command to release ownership (Maintenance to Operator/Program/External/Override). The instruction clears this operand automatically. | Read/Write
PVSD | OCmd_Unlock | BOOL | 0 | Decimal | Operator command to unlock / release (allow Program to acquire) ownership. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | CmdSrc | P_COMMAND_SOURCE | {...} |  | Command source selection. | Read/Write
raP_Dvc_D4SD | HMI_BusObjIndex | DINT | 0 | Decimal | This object's index in the bus array, for use by HMI display. | Read Only
raP_Dvc_D4SD | HMI_eCmdState | SINT | 0 | Decimal | Device target state: 0 = None, 1 = State 0, 2 = State 1, 3 = State 2, 4 = State 3. | Read Only
raP_Dvc_D4SD | HMI_St0PermOK | BOOL | 0 | Decimal | 1 = Permissives are OK to go to State 0. | Read Only
raP_Dvc_D4SD | HMI_St1PermOK | BOOL | 0 | Decimal | 1 = Permissives are OK to go to State 1. | Read Only
raP_Dvc_D4SD | HMI_St2PermOK | BOOL | 0 | Decimal | 1 = Permissives are OK to go to State 2. | Read Only
raP_Dvc_D4SD | HMI_St3PermOK | BOOL | 0 | Decimal | 1 = Permissives are OK to go to State 3. | Read Only
raP_Dvc_D4SD | MCmd_Acq | BOOL | 0 | Decimal | Maintenance Command to acquire Maintenance command source. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance Command to bypass all bypassable interlocks and permissives. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | MCmd_Check | BOOL | 0 | Decimal | Maintenance Command to remove bypass and check all interlocks and permissives. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | MCmd_IS | BOOL | 0 | Decimal | Maintenance Command to select In Service. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | MCmd_OoS | BOOL | 0 | Decimal | Maintenance Command to select Out of Service. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | MCmd_Physical | BOOL | 0 | Decimal | Maintenance Command to select Physical device operation. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | MCmd_Rel | BOOL | 0 | Decimal | Maintenance Command to release Maintenance command source. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance Command to select Virtual device operation. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
raP_Dvc_D4SD | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready for MCmd_Bypass, enable HMI button. | Read Only
raP_Dvc_D4SD | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready for MCmd_Check, enable HMI button. | Read Only
raP_Dvc_D4SD | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
raP_Dvc_D4SD | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
raP_Dvc_D4SD | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
raP_Dvc_D4SD | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
raP_Dvc_D4SD | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
raP_Dvc_D4SD | OCmd_Lock | BOOL | 0 | Decimal | Operator Command to select Operator Locked command source and disallow Program. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | OCmd_Normal | BOOL | 0 | Decimal | Operator Command to select configured normal command source (Operator or Program). The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | OCmd_Oper | BOOL | 0 | Decimal | Operator Command to select Operator (unlocked) command source. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | OCmd_Prog | BOOL | 0 | Decimal | Operator Command to select Program (unlocked) command source. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | OCmd_Reset | BOOL | 0 | Decimal | Operator Command to reset shed latches and returned-to-normal latched alarms. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator Command to acknowledge all alarms and reset latched alarms and shed conditions. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | OCmd_St0 | BOOL | 0 | Decimal | Operator command to set device to State 0. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | OCmd_St1 | BOOL | 0 | Decimal | Operator command to set device to State 1. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | OCmd_St2 | BOOL | 0 | Decimal | Operator command to set device to State 2. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | OCmd_St3 | BOOL | 0 | Decimal | Operator command to set device to State 3. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | OCmd_Unlock | BOOL | 0 | Decimal | Operator Command to unlock Operator command source and allow Program to acquire. The instruction clears this operand automatically. | Read/Write
raP_Dvc_D4SD | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
raP_Dvc_D4SD | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
raP_Dvc_D4SD | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
raP_Dvc_D4SD | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
raP_Dvc_D4SD | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only
raP_Dvc_D4SD | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll, enable HMI button. | Read Only
raP_Dvc_D4SD | ORdy_St0 | BOOL | 0 | Decimal | 1 = Ready for OCmd_St0, enable HMI button. | Read Only
raP_Dvc_D4SD | ORdy_St1 | BOOL | 0 | Decimal | 1 = Ready for OCmd_St1, enable HMI button. | Read Only
raP_Dvc_D4SD | ORdy_St2 | BOOL | 0 | Decimal | 1 = Ready for OCmd_St2, enable HMI button. | Read Only
raP_Dvc_D4SD | ORdy_St3 | BOOL | 0 | Decimal | 1 = Ready for OCmd_St3, enable HMI button. | Read Only
raP_Dvc_D4SD | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
raP_Dvc_LgxChangeDet | HMI_BusObjIndex | DINT | 0 | Decimal | This object's index in the bus array, for use by HMI display. | Read Only
raP_Dvc_LgxChangeDet | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms and latched change detections. The instruction clears this operand automatically. | Read/Write
raP_Dvc_LgxChangeDet | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to acknowledge and reset all alarms and latched change detections. The use of OCmd_ResetAckAll is restricted to HMI. The instruction clears this operand automatically. | Read/Write
raP_Dvc_LgxChangeDet | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only
raP_Dvc_LgxChangeDet | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll, enable HMI button. | Read Only
raP_Dvc_LgxCPU5x80 | Cfg_SupportInfo | STRING_40 | 'Enter software S/N or support contract #' |  | Studio 5000 Logix Designer serial number or support contract identification. | Read/Write
raP_Dvc_LgxCPU5x80 | HMI_BusObjIndex | DINT | 0 | Decimal | This object's index in the bus array, for use by HMI display. | Read Only
raP_Dvc_LgxCPU5x80 | MCmd_Disable | BOOL | 0 | Decimal | Maintenance command to disable collection of data. | Read/Write
raP_Dvc_LgxCPU5x80 | MCmd_Enable | BOOL | 0 | Decimal | Maintenance command to enable collection of data. | Read/Write
raP_Dvc_LgxCPU5x80 | MRdy_Disable | BOOL | 0 | Decimal | 1 = Ready for MCmd_Disable, enable HMI button. | Read Only
raP_Dvc_LgxCPU5x80 | MRdy_Enable | BOOL | 0 | Decimal | 1 = Ready for MCmd_Enable, enable HMI button. | Read Only
raP_Dvc_LgxModuleSts | HMI_BusObjIndex | DINT | 0 | Decimal | This object's index in the bus array, for use by HMI display. | Read Only
raP_Dvc_LgxModuleSts | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance command to bypass checking of the connection state. The instruction clears this operand automatically. | Read/Write
raP_Dvc_LgxModuleSts | MCmd_Check | BOOL | 0 | Decimal | Maintenance command to cancel bypass and have instruction check the connection state. The instruction clears this operand automatically. | Read/Write
raP_Dvc_LgxModuleSts | MCmd_Physical | BOOL | 0 | Decimal | Maintenance command to select Physical module connection status (not simulated). The instruction clears this operand automatically. | Read/Write
raP_Dvc_LgxModuleSts | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance command to select Virtual (simulated) module connection status. The instruction clears this operand automatically. | Read/Write
raP_Dvc_LgxModuleSts | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready for MCmd_Bypass, enable HMI button. | Read Only
raP_Dvc_LgxModuleSts | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready for MCmd_Check, enable HMI button. | Read Only
raP_Dvc_LgxModuleSts | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
raP_Dvc_LgxModuleSts | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
raP_Dvc_LgxModuleSts | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write
raP_Dvc_LgxModuleSts | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to acknowledge and reset all alarms and latched shed conditions. The use of OCmd_ResetAckAll is restricted to HMI. The instruction clears this operand automatically. | Read/Write
raP_Dvc_LgxModuleSts | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only
raP_Dvc_LgxModuleSts | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll, enable HMI button. | Read Only
raP_Dvc_LgxRedun | Cfg_ChasALoc | STRING_32 | 'Upper Chassis' |  | Description of Chassis A Location. | Read/Write
raP_Dvc_LgxRedun | Cfg_ChasBLoc | STRING_32 | 'Lower Chassis' |  | Description of Chassis B Location. | Read/Write
raP_Dvc_LgxRedun | HMI_BusObjIndex | DINT | 0 | Decimal | This object's index in the bus array, for use by HMI display. | Read Only
raP_Dvc_LgxRedun | MCmd_Switchover | BOOL | 0 | Decimal | Maintenance command to initiate switchover to secondary controller. The instruction clears this operand automatically. | Read/Write
raP_Dvc_LgxRedun | MRdy_Switchover | BOOL | 0 | Decimal | 1 = Ready for MCmd_Switchover, enable HMI button. | Read Only
raP_Dvc_LgxRedun | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset cleared latched alarms. The instruction clears this operand automatically. | Read/Write
raP_Dvc_LgxRedun | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to acknowledge all alarms and reset cleared latched alarms. The use of OCmd_ResetAckAll is restricted to HMI. The instruction clears this operand automatically. | Read/Write
raP_Dvc_LgxRedun | OCmd_Sync | BOOL | 0 | Decimal | Operator Command to initiate synchronization of primary to secondary. The instruction clears this operand automatically. | Read/Write
raP_Dvc_LgxRedun | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only
raP_Dvc_LgxRedun | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll, enable HMI button. | Read Only
raP_Dvc_LgxRedun | ORdy_Sync | BOOL | 0 | Decimal | 1 = Ready for OCmd_Sync, enable HMI button. | Read Only
raP_Dvc_LgxTaskMon | HMI_BusObjIndex | DINT | 0 | Decimal | This object's index in the bus array, for use by HMI display. | Read Only
raP_Dvc_LgxTaskMon | MCmd_ClearMaxExecTime | BOOL | 0 | Decimal | Maintenance command to clear maximum execution time. The instruction clears this operand automatically. | Read/Write
raP_Dvc_LgxTaskMon | MCmd_ClearOverlapCount | BOOL | 0 | Decimal | Maintenance command to clear task overlap count. The instruction clears this operand automatically. | Read/Write
raP_Dvc_LgxTaskMon | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset cleared latched alarms. The instruction clears this operand automatically. | Read/Write
raP_Dvc_LgxTaskMon | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to acknowledge all alarms and reset cleared latched alarms. The use of OCmd_ResetAckAll is restricted to HMI. The instruction clears this operand automatically. | Read/Write
raP_Dvc_LgxTaskMon | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only
raP_Dvc_LgxTaskMon | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll, enable HMI button. | Read Only
raP_Dvc_LgxTaskMon | Sts_sName | STRING | '' |  | Task Name as configured in the controller. | Read Only
raP_Dvc_nPos | CmdSrc | P_COMMAND_SOURCE | {...} |  | Control / Command Source Selection | Read/Write
raP_Dvc_nPos | HMI_BusObjIndex | DINT | 0 | Decimal | This object's index in the bus array, for use by HMI display. | Read Only
raP_Dvc_nPos | HMI_eCmdPos | SINT | 0 | Decimal | Last commanded position: 0 = None, 1 = Position 1, 2 = Position 2, ..., 30 = Position 30. | Read Only
raP_Dvc_nPos | MCmd_Acq | BOOL | 0 | Decimal | Maintenance command to acquire ownership (Operator/Program/External/Override to Maintenance). The instruction clears this operand automatically. | Read/Write
raP_Dvc_nPos | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance command to bypass all bypassable interlocks and permissives. The instruction clears this operand automatically. | Read/Write
raP_Dvc_nPos | MCmd_Check | BOOL | 0 | Decimal | Maintenance command to check (not bypass) all interlocks and permissives. The instruction clears this operand automatically. | Read/Write
raP_Dvc_nPos | MCmd_IS | BOOL | 0 | Decimal | Maintenance command to select In service. The instruction clears this operand automatically. | Read/Write
raP_Dvc_nPos | MCmd_OoS | BOOL | 0 | Decimal | Maintenance command to select Out of service. The instruction clears this operand automatically. | Read/Write
raP_Dvc_nPos | MCmd_Physical | BOOL | 0 | Decimal | Maintenance command to select Physical device operation (not simulated). The instruction clears this operand automatically. | Read/Write
raP_Dvc_nPos | MCmd_Rel | BOOL | 0 | Decimal | Maintenance command to release ownership (Maintenance to Operator/Program/External/Override). The instruction clears this operand automatically. | Read/Write
raP_Dvc_nPos | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance command to select Virtual (simulated) device operation. The instruction clears this operand automatically. | Read/Write
raP_Dvc_nPos | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
raP_Dvc_nPos | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready for MCmd_Bypass, enable HMI button. | Read Only
raP_Dvc_nPos | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready for MCmd_Check, enable HMI button. | Read Only
raP_Dvc_nPos | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
raP_Dvc_nPos | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
raP_Dvc_nPos | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
raP_Dvc_nPos | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
raP_Dvc_nPos | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
raP_Dvc_nPos | OCmd_Lock | BOOL | 0 | Decimal | Operator command to lock Operator (disallow Program). The instruction clears this operand automatically. | Read/Write
raP_Dvc_nPos | OCmd_Normal | BOOL | 0 | Decimal | Operator command to select Normal (Operator or Program). The instruction clears this operand automatically. | Read/Write
raP_Dvc_nPos | OCmd_Oper | BOOL | 0 | Decimal | Operator command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write
raP_Dvc_nPos | OCmd_Prog | BOOL | 0 | Decimal | Operator command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write
raP_Dvc_nPos | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write
raP_Dvc_nPos | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to acknowledge and reset all alarms and latched shed conditions. The use of OCmd_ResetAckAll is restricted to HMI. The instruction clears this operand automatically. | Read/Write
raP_Dvc_nPos | OCmd_Unlock | BOOL | 0 | Decimal | Operator command to unlock / release (allow Program to acquire) ownership. The instruction clears this operand automatically. | Read/Write
raP_Dvc_nPos | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
raP_Dvc_nPos | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
raP_Dvc_nPos | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
raP_Dvc_nPos | ORdy_Pos | BOOL | 0 | Decimal | 1 = Ready for OSet_Pos, enable HMI data entry field or command buttons. | Read Only
raP_Dvc_nPos | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
raP_Dvc_nPos | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only
raP_Dvc_nPos | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll, enable HMI button. | Read Only
raP_Dvc_nPos | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
raP_Dvc_nPos | OSet_Pos | SINT | 0 | Decimal | Operator Setting: commanded position 1 to 30, 0 = no change. The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | Cfg_FdbkReqdTable | SINT[11] | {...} | Binary | Table of Feedback Inputs required (checked) to achieve valve State. | Read/Write
raP_Dvc_VlvMP | Cfg_FdbkStateTable | SINT[11] | {...} | Binary | Table of Feedback Input states to achieve valve State. | Read/Write
raP_Dvc_VlvMP | Cfg_FdbkTimeTable | REAL[11] | {...} | Float | Table of times the Feedback must match to confirm valve has reached State. Valid = 0.0 to 60.0 seconds. | Read/Write
raP_Dvc_VlvMP | Cfg_OutStateTable | SINT[11] | {...} | Binary | Table of Output states in given valve State. | Read/Write
raP_Dvc_VlvMP | CmdSrc | P_COMMAND_SOURCE | {...} |  | Command Source. | Read/Write
raP_Dvc_VlvMP | HMI_BusObjIndex | DINT | 0 | Decimal | This object's index in the bus array, for use by HMI display. | Read Only
raP_Dvc_VlvMP | MCmd_Acq | BOOL | 0 | Decimal | Maintenance command to acquire ownership (Operator/Program/External/Override to Maintenance). The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance command to bypass all bypassable interlocks and permissives. The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | MCmd_Check | BOOL | 0 | Decimal | Maintenance command to check (not bypass) all interlocks and permissives. The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | MCmd_IS | BOOL | 0 | Decimal | Maintenance command to select In service. The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | MCmd_OoS | BOOL | 0 | Decimal | Maintenance command to select Out of service. The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | MCmd_Physical | BOOL | 0 | Decimal | Maintenance command to select Physical device operation (not simulated). The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | MCmd_Rel | BOOL | 0 | Decimal | Maintenance command to release ownership (Maintenance to Operator/Program/External/Override). The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance command to select Virtual (simulated) device operation. The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
raP_Dvc_VlvMP | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready for MCmd_Bypass, enable HMI button. | Read Only
raP_Dvc_VlvMP | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready for MCmd_Check, enable HMI button. | Read Only
raP_Dvc_VlvMP | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
raP_Dvc_VlvMP | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
raP_Dvc_VlvMP | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
raP_Dvc_VlvMP | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
raP_Dvc_VlvMP | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
raP_Dvc_VlvMP | OCmd_CleanCavity | BOOL | 0 | Decimal | Operator command to clean valve leakage cavity. The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | OCmd_CleanLower | BOOL | 0 | Decimal | Operator command to clean valve lower seat. The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | OCmd_CleanUpper | BOOL | 0 | Decimal | Operator command to clean valve upper seat. The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | OCmd_Close | BOOL | 0 | Decimal | Operator command to close valve. The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | OCmd_LiftLower | BOOL | 0 | Decimal | Operator command to lift lower valve seat. The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | OCmd_LiftUpper | BOOL | 0 | Decimal | Operator command to lift upper valve seat. The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | OCmd_Lock | BOOL | 0 | Decimal | Operator command to lock Operator (disallow Program). The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | OCmd_Normal | BOOL | 0 | Decimal | Operator command to select Normal (Operator or Program). The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | OCmd_Open | BOOL | 0 | Decimal | Operator command to open valve. The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | OCmd_Oper | BOOL | 0 | Decimal | Operator command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | OCmd_Prog | BOOL | 0 | Decimal | Operator command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms and latched shed conditions. The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to acknowledge and reset all alarms and latched shed conditions. The use of OCmd_ResetAckAll is restricted to HMI. The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | OCmd_Unlock | BOOL | 0 | Decimal | Operator command to unlock / release (allow Program to acquire) ownership. The instruction clears this operand automatically. | Read/Write
raP_Dvc_VlvMP | ORdy_CleanCavity | BOOL | 0 | Decimal | 1 = Ready for OCmd_CleanCavity, enable HMI button. | Read Only
raP_Dvc_VlvMP | ORdy_CleanLower | BOOL | 0 | Decimal | 1 = Ready for OCmd_CleanLower, enable HMI button. | Read Only
raP_Dvc_VlvMP | ORdy_CleanUpper | BOOL | 0 | Decimal | 1 = Ready for OCmd_CleanUpper, enables HMI button. | Read Only
raP_Dvc_VlvMP | ORdy_Close | BOOL | 0 | Decimal | 1 = Ready for OCmd_Close, enable HMI button. | Read Only
raP_Dvc_VlvMP | ORdy_LiftLower | BOOL | 0 | Decimal | 1 = Ready for OCmd_LiftLower, enable HMI button. | Read Only
raP_Dvc_VlvMP | ORdy_LiftUpper | BOOL | 0 | Decimal | 1 = Ready for OCmd_LiftUpper, enable HMI button. | Read Only
raP_Dvc_VlvMP | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
raP_Dvc_VlvMP | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
raP_Dvc_VlvMP | ORdy_Open | BOOL | 0 | Decimal | 1 = Ready for OCmd_Open, enable HMI button. | Read Only
raP_Dvc_VlvMP | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
raP_Dvc_VlvMP | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
raP_Dvc_VlvMP | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only
raP_Dvc_VlvMP | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll, enable HMI button. | Read Only
raP_Dvc_VlvMP | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
raP_Opr_ArbitrationQ | MXRN | BOOL | 1 | Decimal | 1 = Maintenance queue does not exist. | Read/Write
raP_Opr_ArbitrationQ | OXRN | BOOL | 1 | Decimal | 1 = Operator queue does not exist. | Read/Write
raP_Opr_ArbitrationQ | PXRN | BOOL | 1 | Decimal | 1 = Program queue does not exist. | Read/Write
raP_Opr_ArbitrationQ | XXRN | BOOL | 1 | Decimal | 1 = External queue does not exist. | Read/Write
raP_Opr_Area | CmdSrc | P_COMMAND_SOURCE | {...} |  | Control / Command Source Selection. | Read/Write
raP_Opr_Area | HMI_BusObjIndex | DINT | 0 | Decimal | HMI bus object index. | Read Only
raP_Opr_Area | MCmd_Acq | BOOL | 0 | Decimal | Maintenance command to acquire ownership (Operator/Program/External/Override to Maintenance). The instruction clears this operand automatically. | Read/Write
raP_Opr_Area | MCmd_IS | BOOL | 0 | Decimal | Maintenance command to select in service. The instruction clears this operand automatically. | Read/Write
raP_Opr_Area | MCmd_OoS | BOOL | 0 | Decimal | Maintenance command to select out of service. The instruction clears this operand automatically. | Read/Write
raP_Opr_Area | MCmd_Physical | BOOL | 0 | Decimal | Maintenance command to select Physical device operation (not virtualized). | Read/Write
raP_Opr_Area | MCmd_Rel | BOOL | 0 | Decimal | Maintenance command to release ownership (Maintenance to Operator/Program/External/Override). The instruction clears this operand automatically. | Read/Write
raP_Opr_Area | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance command to select Virtual (virtualized) device operation. | Read/Write
raP_Opr_Area | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
raP_Opr_Area | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
raP_Opr_Area | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
raP_Opr_Area | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
raP_Opr_Area | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
raP_Opr_Area | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
raP_Opr_Area | OCmd_Lock | BOOL | 0 | Decimal | Operator command to lock Operator (disallow Program). The instruction clears this operand automatically. | Read/Write
raP_Opr_Area | OCmd_Normal | BOOL | 0 | Decimal | Operator command to select Normal (Operator or Program). The instruction clears this operand automatically. | Read/Write
raP_Opr_Area | OCmd_Oper | BOOL | 0 | Decimal | Operator command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write
raP_Opr_Area | OCmd_OwnerAcq | BOOL | 0 | Decimal | Operator command to acquire child command source. | Read/Write
raP_Opr_Area | OCmd_OwnerRel | BOOL | 0 | Decimal | Operator command to release child command source. | Read/Write
raP_Opr_Area | OCmd_Prog | BOOL | 0 | Decimal | Operator command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write
raP_Opr_Area | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms request. The instruction clears this operand automatically. | Read/Write
raP_Opr_Area | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to reset and acknowledge all alarms. The instruction clears this operand automatically. | Read/Write
raP_Opr_Area | OCmd_Unlock | BOOL | 0 | Decimal | Operator command to unlock or release (allow Program to acquire) ownership. The instruction clears this operand automatically. | Read/Write
raP_Opr_Area | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
raP_Opr_Area | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
raP_Opr_Area | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
raP_Opr_Area | ORdy_OwnerAcq | BOOL | 0 | Decimal | 1 = Ready for OCmd_OwnerAcq, enable HMI button. | Read Only
raP_Opr_Area | ORdy_OwnerRel | BOOL | 0 | Decimal | 1 = Ready for OCmd_OwnerRel, enable HMI button. | Read Only
raP_Opr_Area | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
raP_Opr_Area | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only
raP_Opr_Area | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll, enable HMI button. | Read Only
raP_Opr_Area | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
raP_Opr_EMGen | CmdSrc | P_COMMAND_SOURCE | {...} |  | Control / Command Source Selection. | Read/Write
raP_Opr_EMGen | HMI_BusObjIndex | DINT | 0 | Decimal | HMI bus object index. | Read Only
raP_Opr_EMGen | MCmd_Acq | BOOL | 0 | Decimal | Maintenance command to acquire ownership (Operator/Program/External/Override to Maintenance). The instruction clears this operand automatically. | Read/Write
raP_Opr_EMGen | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance command to bypass all bypassable interlocks and permissives. The instruction clears this operand automatically. | Read/Write
raP_Opr_EMGen | MCmd_Check | BOOL | 0 | Decimal | Maintenance command to check (not bypass) all interlocks and permissives. The instruction clears this operand automatically. | Read/Write
raP_Opr_EMGen | MCmd_IS | BOOL | 0 | Decimal | Maintenance command to select in service. The instruction clears this operand automatically. | Read/Write
raP_Opr_EMGen | MCmd_OoS | BOOL | 0 | Decimal | Maintenance command to select out of service. The instruction clears this operand automatically. | Read/Write
raP_Opr_EMGen | MCmd_Rel | BOOL | 0 | Decimal | Maintenance command to release ownership (Maintenance to Operator/Program/External/Override). The instruction clears this operand automatically. | Read/Write
raP_Opr_EMGen | MCmd_StateForce | BOOL | 0 | Decimal | Maintenance command to force state request. The instruction clears this operand automatically. | Read/Write
raP_Opr_EMGen | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
raP_Opr_EMGen | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready for MCmd_Bypass, enable HMI button. | Read Only
raP_Opr_EMGen | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready for MCmd_Check, enable HMI button. | Read Only
raP_Opr_EMGen | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
raP_Opr_EMGen | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
raP_Opr_EMGen | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
raP_Opr_EMGen | MRdy_StateForce | BOOL | 0 | Decimal | 1 = Ready for MCmd_StateForce, enable HMI button. | Read Only
raP_Opr_EMGen | MRdy_Step | BOOL | 0 | Decimal | 1 = Ready to receive MSet_Step. | Read Only
raP_Opr_EMGen | MSet_Step | INT | 0 | Decimal | Maintenance setting for process step number request. | Read/Write
raP_Opr_EMGen | OCmd | DINT | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | Operator command to State. (x) The instruction clears this operand automatically. | Read/Write
raP_Opr_EMGen | OCmd_Lock | BOOL | 0 | Decimal | Operator command to lock Operator (disallow Program). The instruction clears this operand automatically. | Read/Write
raP_Opr_EMGen | OCmd_Normal | BOOL | 0 | Decimal | Operator command to select normal (Operator or Program). The instruction clears this operand automatically. | Read/Write
raP_Opr_EMGen | OCmd_Oper | BOOL | 0 | Decimal | Operator command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write
raP_Opr_EMGen | OCmd_OwnerAcq | BOOL | 0 | Decimal | Operator command to acquire child command source. | Read/Write
raP_Opr_EMGen | OCmd_OwnerRel | BOOL | 0 | Decimal | Operator command to release child command source. | Read/Write
raP_Opr_EMGen | OCmd_ParCapture | SINT | 0 | Decimal | Operator command to capture initial parameter. The instruction clears this operand automatically. Bit: 0 - Param 1 - 16 1 - Param 17 - 32 2 - Param 33 - 48. | Read/Write
raP_Opr_EMGen | OCmd_ParClear | SINT | 0 | Decimal | Operator command to clear parameter. The instruction clears this operand automatically. Bit: 0 - Param 1 - 16 1 - Param 17 - 32 2 - Param 33 - 48. | Read/Write
raP_Opr_EMGen | OCmd_ParRestore | SINT | 0 | Decimal | Operator command to restore initial parameter. The instruction clears this operand automatically. Bit: 0 - Param 1 - 16 1 - Param 17 - 32 2 - Param 33 - 48. | Read/Write
raP_Opr_EMGen | OCmd_Prog | BOOL | 0 | Decimal | Operator command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write
raP_Opr_EMGen | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms request. The instruction clears this operand automatically. | Read/Write
raP_Opr_EMGen | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to reset and acknowledge all alarms. The instruction clears this operand automatically. | Read/Write
raP_Opr_EMGen | OCmd_RptCapture | SINT | 0 | Decimal | Operator command to capture initial report. The instruction clears this operand automatically. Bit: 0 - Rpt 1 - 16 1 - Rpt 17 - 32 2 - Rpt 33 - 48. | Read/Write
raP_Opr_EMGen | OCmd_RptClear | SINT | 0 | Decimal | Operator command to clear report. The instruction clears this operand automatically. Bit: 0 - Rpt 1 - 16 1 - Rpt 17 - 32 2 - Rpt 33 - 48. | Read/Write
raP_Opr_EMGen | OCmd_RptRestore | SINT | 0 | Decimal | Operator command to restore initial report. The instruction clears this operand automatically. Bit: 0 - Rpt 1 - 16 1 - Rpt 17 - 32 2 - Rpt 33 - 48. | Read/Write
raP_Opr_EMGen | OCmd_Unlock | BOOL | 0 | Decimal | Operator command to unlock / release (allow Program to acquire) ownership. The instruction clears this operand automatically. | Read/Write
raP_Opr_EMGen | ORdy | DINT | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 1 = Ready for OCmd_(x), enable HMI button. | Read Only
raP_Opr_EMGen | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
raP_Opr_EMGen | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
raP_Opr_EMGen | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
raP_Opr_EMGen | ORdy_OwnerAcq | BOOL | 0 | Decimal | 1 = Ready for OCmd_OwnerAcq, enable HMI button. | Read Only
raP_Opr_EMGen | ORdy_OwnerRel | BOOL | 0 | Decimal | 1 = Ready for OCmd_OwnerRel, enable HMI button. | Read Only
raP_Opr_EMGen | ORdy_ParCapture | BOOL | 0 | Decimal | 1 = Ready for OCmd_ParCapture, enable HMI button. | Read Only
raP_Opr_EMGen | ORdy_ParClear | BOOL | 0 | Decimal | 1 = Ready for OCmd_ParClear, enable HMI button. | Read Only
raP_Opr_EMGen | ORdy_ParRestore | BOOL | 0 | Decimal | 1 = Ready for OCmd_ParRestore, enable HMI button. | Read Only
raP_Opr_EMGen | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
raP_Opr_EMGen | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only
raP_Opr_EMGen | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll, enable HMI button. | Read Only
raP_Opr_EMGen | ORdy_RptCapture | BOOL | 0 | Decimal | 1 = Ready for OCmd_RptCapture, enable HMI button. | Read Only
raP_Opr_EMGen | ORdy_RptClear | BOOL | 0 | Decimal | 1 = Ready for OCmd_RptClear, enable HMI button. | Read Only
raP_Opr_EMGen | ORdy_RptRestore | BOOL | 0 | Decimal | 1 = Ready for OCmd_RptRestore, enable HMI button. | Read Only
raP_Opr_EMGen | ORdy_State | DINT | 2#0000_0000_0000_0000_0000_0000_0000_0000 | Binary | 1 = Ready for OCmd.(x), enable parameter. | Read Only
raP_Opr_EMGen | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
raP_Opr_EMGen | StateMachine | raP_Opr_VSM | {...} |  | Configurable State Machine, Max 32 states and commands. | Read/Write
raP_Opr_EPGen | Cfg_ShedOnIntlk | BOOL | 2#1 | Binary | 1 = Stop equipment phase and alarm on interlock trip; 0 = Stop equipment phase. | Read/Write
raP_Opr_EPGen | CmdSrc | P_COMMAND_SOURCE | {...} |  | Control / Command Source Selection. | Read/Write
raP_Opr_EPGen | HMI_AlwaysCnfrmReqd | SINT | 0 | Decimal | Always require confirm for Abort | Read Only
raP_Opr_EPGen | HMI_BusObjIndex | DINT | 0 | Decimal | HMI bus object index. | Read Only
raP_Opr_EPGen | MCmd_Acq | BOOL | 0 | Decimal | Maintenance command to acquire ownership (Operator/Program/External/Override to Maintenance). The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance command to bypass all bypassable interlocks and permissives. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | MCmd_Check | BOOL | 0 | Decimal | Maintenance command to check (not bypass) all interlocks and permissives. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | MCmd_IS | BOOL | 0 | Decimal | Maintenance command to select in service. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | MCmd_OoS | BOOL | 0 | Decimal | Maintenance command to select out of service. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | MCmd_Rel | BOOL | 0 | Decimal | Maintenance command to release ownership (Maintenance to Operator/Program/External/Override). The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | MCmd_StateForce | BOOL | 0 | Decimal | Maintenance command to force state request. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
raP_Opr_EPGen | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready for MCmd_Bypass, enable HMI button. | Read Only
raP_Opr_EPGen | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready for MCmd_Check, enable HMI button. | Read Only
raP_Opr_EPGen | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
raP_Opr_EPGen | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
raP_Opr_EPGen | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
raP_Opr_EPGen | MRdy_StateForce | BOOL | 0 | Decimal | 1 = Ready for MCmd_StateForce, enable HMI button. | Read Only
raP_Opr_EPGen | MRdy_Step | BOOL | 0 | Decimal | 1 = Ready to receive MSet_Step, enable HMI entry field. | Read Only
raP_Opr_EPGen | MSet_Step | INT | 0 | Decimal | Maintenance setting for process step number request. | Read/Write
raP_Opr_EPGen | OCmd_Abort | BOOL | 0 | Decimal | Operator command to abort request. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | OCmd_AutoPause | BOOL | 0 | Decimal | Operator command to auto pause request. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | OCmd_Hold | BOOL | 0 | Decimal | Operator command to hold request. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | OCmd_Lock | BOOL | 0 | Decimal | Operator command to lock Operator (disallow Program). The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | OCmd_Normal | BOOL | 0 | Decimal | Operator command to select normal (Operator or Program). The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | OCmd_Oper | BOOL | 0 | Decimal | Operator command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | OCmd_OwnerAcq | BOOL | 0 | Decimal | Operator command to acquire child command source. | Read/Write
raP_Opr_EPGen | OCmd_OwnerRel | BOOL | 0 | Decimal | Operator command to release child command source. | Read/Write
raP_Opr_EPGen | OCmd_ParCapture | SINT | 0 | Decimal | Operator command to capture initial parameter. The instruction clears this operand automatically. Bit: 0 - Param 1 - 16 1 - Param 17 - 32 2 - Param 33 - 48. | Read/Write
raP_Opr_EPGen | OCmd_ParClear | SINT | 0 | Decimal | Operator command to clear parameter. The instruction clears this operand automatically. Bit: 0 - Param 1 - 16 1 - Param 17 - 32 2 - Param 33 - 48. | Read/Write
raP_Opr_EPGen | OCmd_ParRestore | SINT | 0 | Decimal | Operator command to restore initial parameter. The instruction clears this operand automatically. Bit: 0 - Param 1 - 16 1 - Param 17 - 32 2 - Param 33 - 48. | Read/Write
raP_Opr_EPGen | OCmd_Pause | BOOL | 0 | Decimal | Operator command to pause request. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | OCmd_Prog | BOOL | 0 | Decimal | Operator command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms request. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to reset and acknowledge all alarms. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | OCmd_ResetPhs | BOOL | 0 | Decimal | Operator command to reset phase request. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | OCmd_Restart | BOOL | 0 | Decimal | Operator command to restart request. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | OCmd_Resume | BOOL | 0 | Decimal | Operator command to resume from paused request. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | OCmd_RptCapture | SINT | 0 | Decimal | Operator command to capture initial report. The instruction clears this operand automatically. Bit: 0 - Rpt 1 - 16 1 - Rpt 17 - 32 2 - Rpt 33 - 48. | Read/Write
raP_Opr_EPGen | OCmd_RptClear | SINT | 0 | Decimal | Operator command to clear report. The instruction clears this operand automatically. Bit: 0 - Rpt 1 - 16 1 - Rpt 17 - 32 2 - Rpt 33 - 48. | Read/Write
raP_Opr_EPGen | OCmd_RptRestore | SINT | 0 | Decimal | Operator command to restore initial report. The instruction clears this operand automatically. Bit: 0 - Rpt 1 - 16 1 - Rpt 17 - 32 2 - Rpt 33 - 48. | Read/Write
raP_Opr_EPGen | OCmd_Start | BOOL | 0 | Decimal | Operator command to start Request. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | OCmd_Stop | BOOL | 0 | Decimal | Operator command to stop request. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | OCmd_Unlock | BOOL | 0 | Decimal | Operator command to unlock / release (allow Program to acquire) ownership. The instruction clears this operand automatically. | Read/Write
raP_Opr_EPGen | ORdy_Abort | BOOL | 0 | Decimal | 1 = Ready for OCmd_Abort, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_AutoPause | BOOL | 0 | Decimal | 1 = Ready for OCmd_AutoPause, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_Hold | BOOL | 0 | Decimal | 1 = Ready for OCmd_Hold, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_OwnerAcq | BOOL | 0 | Decimal | 1 = Ready for OCmd_OwnerRel, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_OwnerRel | BOOL | 0 | Decimal | 1 = Ready for OCmd_OwnerOper, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_ParCapture | BOOL | 0 | Decimal | 1 = Ready for OCmd_ParCapture, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_ParClear | BOOL | 0 | Decimal | 1 = Ready for OCmd_ParClear, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_ParRestore | BOOL | 0 | Decimal | 1 = Ready for OCmd_ParRestore, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_Pause | BOOL | 0 | Decimal | 1 = Ready for OCmd_Pause, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_ResetPhs | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetPhs, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_Restart | BOOL | 0 | Decimal | 1 = Ready for OCmd_Restart, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_Resume | BOOL | 0 | Decimal | 1 = Ready for OCmd_Resume, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_RptCapture | BOOL | 0 | Decimal | 1 = Ready for OCmd_RptCapture, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_RptClear | BOOL | 0 | Decimal | 1 = Ready for OCmd_RptClear, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_RptRestore | BOOL | 0 | Decimal | 1 = Ready for OCmd_RptRestore, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_Start | BOOL | 0 | Decimal | 1 = Ready for OCmd_Start, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_Stop | BOOL | 0 | Decimal | 1 = Ready for OCmd_Stop, enable HMI button. | Read Only
raP_Opr_EPGen | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
raP_Opr_ExtddAlm | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset cleared latched alarms. The instruction clears this operand automatically. | Read/Write
raP_Opr_ExtddAlm | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to acknowledge and reset all alarms. The use of OCmd_ResetAckAll is restricted to HMI. The instruction clears this operand automatically. | Read/Write
raP_Opr_ExtddAlm | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only
raP_Opr_ExtddAlm | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll, enable HMI button. | Read Only
raP_Opr_OrgScan | Cfg_EditTimeOut | DINT | 120 | Decimal | Timeout to release edit owner when no edits are detected. | Read/Write
raP_Opr_OrgView | HMI | raP_UDT_Opr_Bus_View[25] | {...} |  | UDT array to hold each tree node visibility characteristics. | Read/Write
raP_Opr_OrgView | HMI_Cfg | BOOL | 0 | Decimal | Config for HMI use. | Read/Write
raP_Opr_OrgView | MyDA | DINT[7] | {...} | Decimal | GSV data to create a unique ID. | Read Only
raP_Opr_OrgView | Name | STRING_16 | '' |  | Name of this client. | Read/Write
raP_Opr_OrgView | OCmd_PageNext | BOOL | 0 | Decimal | Operator command to page the view forward. The instruction clears this operand automatically. | Read/Write
raP_Opr_OrgView | OCmd_PagePrevious | BOOL | 0 | Decimal | Operator command to page the view back. The instruction clears this operand automatically. | Read/Write
raP_Opr_OrgView | OCmd_PageTop | BOOL | 0 | Decimal | Operator command to set the view to the first page. The instruction clears this operand automatically. | Read/Write
raP_Opr_OrgView | ORdy_PageNext | BOOL | 0 | Decimal | Ready to go to the next page. 1 = Ready for OCmd_PageNext, enable HMI button. | Read/Write
raP_Opr_OrgView | ORdy_PagePrevious | BOOL | 0 | Decimal | Ready to go to the previous page. 1 = Ready for OCmd_PagePrevious, enable HMI button. | Read/Write
raP_Opr_OrgView | ORdy_PageTop | BOOL | 0 | Decimal | Ready to go to the first page. 1 = Ready for OCmdPageTop, enable HMI button. | Read/Write
raP_Opr_OrgView | OSet_CmdEC | DINT | -1 | Decimal | Expand/Collapse the HMI index entered (Reset to -1 after action) | Read/Write
raP_Opr_OrgView | Set_ViewStartNode | DINT | 0 | Decimal | Node number in the node array to start this view (0 <= x <= LastNodeUsed). | Read/Write
raP_Opr_OrgView | Visible | BOOL[1024] | {...} | Decimal | Visibility array corresponds to the Node Array. 1 = Visible. | Read/Write
raP_Opr_Owner | Cfg_TimeOutThreshold | DINT | 1048576 | Decimal | Number of execution counts before declaring a missing CmdSrc or ArbitrationQ. | Read/Write
raP_Opr_Prompt | HMI_BusObjIndex | DINT | 0 | Decimal | Bus array element number. | Read Only
raP_Opr_Prompt | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset latched alarm. The controller clears this operand automatically. | Read/Write
raP_Opr_Prompt | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to reset and acknowledge alarm. The controller clears this operand automatically. | Read/Write
raP_Opr_Prompt | Prompt | raP_Opr_Prompt_Core | {...} |  | Operator Prompt Core. | Read/Write
raP_Opr_Prompt_Core | HMI_AlrtCnfrm | BOOL | 0 | Decimal |  | Read Only
raP_Opr_Prompt_Core | HMI_AlrtDispVal | SINT | 0 | Decimal |  | Read Only
raP_Opr_Prompt_Core | HMI_AlrtInpVal | SINT | 0 | Decimal | A required input value has not been entered. | Read Only
raP_Opr_Prompt_Core | HMI_AlrtResp | SINT | 0 | Decimal |  | Read Only
raP_Opr_Prompt_Core | HMI_AlrtSelect | BOOL | 0 | Decimal |  | Read Only
raP_Opr_Prompt_Core | HMI_None | STRING_16 | '<None>' |  | Static string '<None>' | None
raP_Opr_Prompt_Core | HMI_NotInit | DINT | -2147483648 | Decimal |  | Read Only
raP_Opr_Prompt_Core | HMI_nullString | STRING_16 | '' |  | Nul string constatnt | None
raP_Opr_Prompt_Core | Init | BOOL | 0 | Decimal |  | Read/Write
raP_Opr_Prompt_Core | Inp_Real | REAL[4] | {...} | Float |  | Read/Write
raP_Opr_Prompt_Core | OCmd_Cnfrm | BOOL | 0 | Decimal | Operator Confirmation. | Read/Write
raP_Opr_Prompt_Core | ORdy_Cnfrm | BOOL | 0 | Decimal | 1 = Prompt Ready for Operator Confirmation. | Read Only
raP_Opr_Prompt_Core | OSet_DispValVrfy | SINT | 0 | Decimal |  | Read/Write
raP_Opr_Prompt_Core | OSet_RealOut | REAL[4] | {...} | Float |  | Read/Write
raP_Opr_Prompt_Core | OSet_Resp | STRING_40[4] | {...} |  |  | Read/Write
raP_Opr_Prompt_Core | OSet_Select | SINT | 4 | Decimal |  | Read/Write
raP_Opr_Prompt_Core | Out_Real | REAL[4] | {...} | Float |  | Read Only
raP_Opr_Prompt_Core | Prompt | raP_UDT_Opr_PromptCfg | {...} |  | Prompt Instance Configuration Data | Read/Write
raP_Opr_Prompt_Core | Val_DispReal | REAL[4] | {...} | Float |  | Read Only
raP_Opr_Prompt_Core | Val_MaxPromptIdx | DINT | 0 | Decimal |  | Read Only
raP_Opr_Seq | Cfg_SM | raP_UDT_Opr_VSM_Cfg | {...} |  | Variable State Machine Configuration Parameters | Read/Write
raP_Opr_Seq | CmdSrc | P_COMMAND_SOURCE | {...} |  | Command Source | Read/Write
raP_Opr_Seq | HMI_AbsStepNum | INT[9] | {...} | Decimal | Detail absolute step numbers | Read Only
raP_Opr_Seq | HMI_AlwaysCnfrmReqd | SINT | 0 | Decimal | Always require confirm for Abort | Read Only
raP_Opr_Seq | HMI_BranchTargetName | STRING_20[9] | {...} |  | Detail branch target names | Read Only
raP_Opr_Seq | HMI_BranchTargetStepNum | INT[9] | {...} | Decimal | Detail Branch Target Step Number | Read Only
raP_Opr_Seq | HMI_BranchType | SINT[9] | {...} | Decimal | Detail branch types | Read Only
raP_Opr_Seq | HMI_BusObjIndex | DINT | 0 | Decimal | Bus index used for this object | Read Only
raP_Opr_Seq | HMI_BusOwnObjIndex | DINT | 0 | Decimal | Bus index used for this object's owner | Read Only
raP_Opr_Seq | HMI_CurrentPosition | INT | 0 | Decimal | Detail Current Position | Read Only
raP_Opr_Seq | HMI_DtlVis | DINT | 0 | Decimal | Detail Step Visibility Flags | Read Only
raP_Opr_Seq | HMI_HasInSeqTimeOut | BOOL | 0 | Decimal | Has In Sequence Time Out Flag | Read Only
raP_Opr_Seq | HMI_HasInStateTimeOut | BOOL | 0 | Decimal | Has In State Time Out Flag | Read Only
raP_Opr_Seq | HMI_HasInStepTimeOut | BOOL | 0 | Decimal | Has In Step TimeOut Flag | Read Only
raP_Opr_Seq | HMI_LoopBranchCount | INT[9] | {...} | Decimal | Detail Current Loop Branch Counter | Read Only
raP_Opr_Seq | HMI_LoopBranchLim | INT[9] | {...} | Decimal | Detail Current Loop Branch Limit | Read Only
raP_Opr_Seq | HMI_NextState | SINT | 0 | Decimal | Numerical value of next state after resume | Read Only
raP_Opr_Seq | HMI_NextStepAbs | INT | 0 | Decimal | Numerical value of next absolute step after resume | Read Only
raP_Opr_Seq | HMI_NextStepInState | INT | 0 | Decimal | Numerical value of next step after resume | Read Only
raP_Opr_Seq | HMI_NumStepsInEditState | INT | 0 | Decimal | HMI Number of steps in the current Edit State | Read Only
raP_Opr_Seq | HMI_Pause | INT | 0 | Decimal | Detail pause state | Read Only
raP_Opr_Seq | HMI_QtyVis | BOOL | 0 | Decimal | Quantity Visibility Flag | Read Only
raP_Opr_Seq | HMI_StateOverSeq | BOOL | 0 | Decimal | State or Sequence Time Out Visibility Flag | Read Only
raP_Opr_Seq | HMI_StepName | STRING_20[9] | {...} |  | Detail relative step names | Read Only
raP_Opr_Seq | HMI_StepNum | INT[9] | {...} | Decimal | Detail relative step numbers | Read Only
raP_Opr_Seq | MCmd_Acq | BOOL | 0 | Decimal | Maintenance Acquire Request | Read/Write
raP_Opr_Seq | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance Bypass Request | Read/Write
raP_Opr_Seq | MCmd_Check | BOOL | 0 | Decimal | Maintenance Check Request | Read/Write
raP_Opr_Seq | MCmd_IS | BOOL | 0 | Decimal | Maintenance In Service Request | Read/Write
raP_Opr_Seq | MCmd_OoS | BOOL | 0 | Decimal | Maintenance Out of Service Request | Read/Write
raP_Opr_Seq | MCmd_SeqStepForce | BOOL | 0 | Decimal | Maintenance Step Force Request | Read/Write
raP_Opr_Seq | MCmd_StepTimerForce | BOOL | 0 | Decimal | Maintenance Step Timer Force Request | Read/Write
raP_Opr_Seq | MRdy_Acq | BOOL | 0 | Decimal | Maintenance Acquire Ready | Read Only
raP_Opr_Seq | MRdy_Bypass | BOOL | 0 | Decimal | Maintenance Bypass Ready | Read Only
raP_Opr_Seq | MRdy_Check | BOOL | 0 | Decimal | Maintenance Check Ready | Read Only
raP_Opr_Seq | MRdy_IS | BOOL | 0 | Decimal | Maintenance In Service Ready | Read Only
raP_Opr_Seq | MRdy_OoS | BOOL | 0 | Decimal | Maintenance Out of Service Ready | Read Only
raP_Opr_Seq | MRdy_Rel | BOOL | 0 | Decimal | Maintenance release Ready | Read Only
raP_Opr_Seq | MRdy_SeqStepForce | BOOL | 0 | Decimal | Maintenance Step Force Ready | Read Only
raP_Opr_Seq | MSet_SingleStep | BOOL | 0 | Decimal | Maintenance Single Step Request | Read/Write
raP_Opr_Seq | OCmd_Lock | BOOL | 0 | Decimal | Operator Lock Request | Read/Write
raP_Opr_Seq | OCmd_Normal | BOOL | 0 | Decimal | Operator Normal Request | Read/Write
raP_Opr_Seq | OCmd_Oper | BOOL | 0 | Decimal | Operator Operator Request | Read/Write
raP_Opr_Seq | OCmd_Prog | BOOL | 0 | Decimal | Operator Program Request | Read/Write
raP_Opr_Seq | OCmd_Reset | BOOL | 0 | Decimal | Operator Reset Request | Read/Write
raP_Opr_Seq | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator Reset Acknowlege All Request | Read/Write
raP_Opr_Seq | OCmd_SeqAbort | BOOL | 0 | Decimal | Operator Sequence Abort Command | Read/Write
raP_Opr_Seq | OCmd_SeqAutoPause | BOOL | 0 | Decimal | Operator Auto Pause Request | Read/Write
raP_Opr_Seq | OCmd_SeqCancelPause | BOOL | 0 | Decimal | Operator Cancel Pause request | Read/Write
raP_Opr_Seq | OCmd_SeqClear | BOOL | 0 | Decimal | Operator Sequence Clear Command | Read/Write
raP_Opr_Seq | OCmd_SeqComplete | BOOL | 0 | Decimal | Operator Sequence Complete Request | Read/Write
raP_Opr_Seq | OCmd_SeqHold | BOOL | 0 | Decimal | Operator Sequence Hold Request | Read/Write
raP_Opr_Seq | OCmd_SeqPause | BOOL | 0 | Decimal | Operator Pause Request | Read/Write
raP_Opr_Seq | OCmd_SeqReset | BOOL | 0 | Decimal | Operator Sequence Reset Command | Read/Write
raP_Opr_Seq | OCmd_SeqRestart | BOOL | 0 | Decimal | Operator Sequence Restart Command | Read/Write
raP_Opr_Seq | OCmd_SeqResume | BOOL | 0 | Decimal | Operator Resume Request | Read/Write
raP_Opr_Seq | OCmd_SeqStart | BOOL | 0 | Decimal | Operator Sequence Start Request | Read/Write
raP_Opr_Seq | OCmd_SeqStop | BOOL | 0 | Decimal | Operator Sequence Stop Command | Read/Write
raP_Opr_Seq | OCmd_SeqSuspend | BOOL | 0 | Decimal | Operator Sequence Suspend Command | Read/Write
raP_Opr_Seq | OCmd_SeqUnSuspend | BOOL | 0 | Decimal | Operator Sequence Unsuspend Command | Read/Write
raP_Opr_Seq | OCmd_StdQtyReset | BOOL | 0 | Decimal | Operator Quantity Value Reset Request | Read/Write
raP_Opr_Seq | OCmd_Unlock | BOOL | 0 | Decimal | Operator Unlock Request | Read/Write
raP_Opr_Seq | ORdy_Lock | BOOL | 0 | Decimal | Ready for OCmd_Lock | Read Only
raP_Opr_Seq | ORdy_Normal | BOOL | 0 | Decimal | Ready for OCmd_Normal | Read Only
raP_Opr_Seq | ORdy_Oper | BOOL | 0 | Decimal | Ready for OCmd_Oper | Read Only
raP_Opr_Seq | ORdy_Prog | BOOL | 0 | Decimal | Ready for OCmd_Prog | Read Only
raP_Opr_Seq | ORdy_Qty | BOOL | 0 | Decimal | Ready for OCmd_Qty | Read Only
raP_Opr_Seq | ORdy_Reset | BOOL | 0 | Decimal | Ready for OCmd_Reset | Read Only
raP_Opr_Seq | ORdy_ResetAckAll | BOOL | 0 | Decimal | Ready for OCmd_Reset Acknowlege All | Read Only
raP_Opr_Seq | ORdy_SeqAbort | BOOL | 0 | Decimal | Ready for OCmd_SeqAbort | Read Only
raP_Opr_Seq | ORdy_SeqAutoPause | BOOL | 0 | Decimal | Ready for OCmd_SeqAutoPause | Read Only
raP_Opr_Seq | ORdy_SeqCancelPause | BOOL | 0 | Decimal | Ready for OCmd_SeqCancelPause | Read Only
raP_Opr_Seq | ORdy_SeqClear | BOOL | 0 | Decimal | Ready for OCmd_SeqClear | Read Only
raP_Opr_Seq | ORdy_SeqComplete | BOOL | 0 | Decimal | Ready for OCmd_SeqComplete | Read Only
raP_Opr_Seq | ORdy_SeqHold | BOOL | 0 | Decimal | Ready for OCmd_SeqHold | Read Only
raP_Opr_Seq | ORdy_SeqPause | BOOL | 0 | Decimal | Ready for OCmd_SeqPause | Read Only
raP_Opr_Seq | ORdy_SeqReset | BOOL | 0 | Decimal | Ready for OCmd_SeqReset | Read Only
raP_Opr_Seq | ORdy_SeqRestart | BOOL | 0 | Decimal | Ready for OCmd_SeqRestart | Read Only
raP_Opr_Seq | ORdy_SeqResume | BOOL | 0 | Decimal | Ready for OCmd_SeqResume | Read Only
raP_Opr_Seq | ORdy_SeqStart | BOOL | 0 | Decimal | Ready for OCmd_SeqStart | Read Only
raP_Opr_Seq | ORdy_SeqStop | BOOL | 0 | Decimal | Ready for OCmd_SeqStop | Read Only
raP_Opr_Seq | ORdy_SeqSuspend | BOOL | 0 | Decimal | Ready for OCmd_SeqSuspend | Read Only
raP_Opr_Seq | ORdy_SeqUnsuspend | BOOL | 0 | Decimal | Ready for OCmd_SeqUnsuspend | Read Only
raP_Opr_Seq | ORdy_StdQtyReset | BOOL | 0 | Decimal | Ready for OCmd_StdQtyReset | Read Only
raP_Opr_Seq | ORdy_Unlock | BOOL | 0 | Decimal | Ready for OCmd_Unlock | Read Only
raP_Opr_Seq | OSet_Qty | INT | 0 | Decimal | Operator quantity entry | Read/Write
raP_Opr_Seq | SeqState | raP_UDT_Opr_SeqState[17] | {...} |  | Data for one raP_Opr_Seq State | Read/Write
raP_Opr_Seq | StateMachine | raP_Opr_VSM | {...} |  | Variable State Machine 32 Max States 32 Max Commands | Read/Write
raP_Opr_Seq | Sts_CurrStepHasTimer | BOOL | 0 | Decimal | Detail current step has timer | Read Only
raP_Opr_Seq | Sts_CurrStepTimerConfig | BOOL | 0 | Decimal | Detail current step timer config | Read Only
raP_Opr_Seq | Val_CurrStepName | STRING_20 | '' |  | Current Step Name Buffer | Read Only
raP_Opr_Seq | Val_CurrStepNum | INT | 0 | Decimal | Current Step Number | Read Only
raP_Opr_Seq | Val_NextStepName | STRING_20 | '' |  | Name of next step | Read Only
raP_Opr_Seq | Val_NumStepsInCurrState | INT | 0 | Decimal | Number of Steps in Current State | Read Only
raP_Opr_SeqBoolInp | Cfg_bHasInp | INT[8] | {...} | Binary | Bits=1 Corresponding input exists | Read/Write
raP_Opr_SeqBoolInp | Cfg_bHasInpNav | INT[8] | {...} | Binary | Bits=1 indicate inputs with navigation enabled | Read/Write
raP_Opr_SeqBoolInp | Cfg_bInpForceMask | INT[8] | {...} | Binary | Bits=1 Corresponding input can be forced | Read/Write
raP_Opr_SeqBoolInp | Cfg_bUseInp | INT[8] | {...} | Binary | Bits=1 Corresponding input is used | Read/Write
raP_Opr_SeqBoolInp | HMI_bForceEN | INT[8] | {...} | Decimal | Bits=1 Corresponding input can be forced | Read Only
raP_Opr_SeqBoolInp | HMI_bWaitingForInputsHasNav | INT | 0 | Decimal | Bits=1 Corresponding input has navigation | Read/Write
raP_Opr_SeqBoolInp | HMI_CurrStepHasInpBank | SINT | 0 | Decimal | Bit mapped current step has inputs in these banks | Read Only
raP_Opr_SeqBoolInp | HMI_CurrStepWaitingOnBank | SINT | 0 | Decimal | Bit mapped current step is waiting for inputs in these banks | Read Only
raP_Opr_SeqBoolInp | HMI_WaitingForInputCnt | SINT | 0 | Decimal | Number(s) of inputs that are unqualified | Read Only
raP_Opr_SeqBoolInp | HMI_WaitingForInputsBank | SINT[16] | {...} | Decimal | Bank number(s) with unqualified inputs | Read Only
raP_Opr_SeqBoolInp | HMI_WaitingForInputsBit | SINT[16] | {...} | Decimal | Bits=1 Corresponding input is unqualified | Read Only
raP_Opr_SeqBoolInp | MCmd_bInpForce | INT[8] | {...} | Binary | Maintenance command to force the corresponding input | Read/Write
raP_Opr_SeqBoolInp | Sts_bCurrStepHasInput | INT[8] | {...} | Decimal | Bits=1 Has corresponding input | Read Only
raP_Opr_SeqBoolInp | Sts_bCurrStepQualifyState | INT[8] | {...} | Decimal | Bits=1 Corresponding input's qualification state | Read Only
raP_Opr_SeqBoolInp | Sts_bInpForced | INT[8] | {...} | Decimal | Bits=1 Corresponding input is forced | Read Only
raP_Opr_SeqBoolInp | Sts_bQualified | INT[8] | {...} | Decimal | Bits=1 Corresponding input(s) are qualified | Read Only
raP_Opr_SeqBoolInp | Sts_bQualifyLost | INT[8] | {...} | Decimal | Bits=1 Corresponding input qualification was lost | Read Only
raP_Opr_SeqBoolInp | Val_MaxBankIndex | SINT | 0 | Decimal | Maximum Bank Index | Read Only
raP_Opr_SeqBoolOut | Cfg_bHasOutNav | INT[8] | {...} | Decimal | Bits=1 indicate inputs with navigation enabled | Read/Write
raP_Opr_SeqBoolOut | Cfg_bTracking | INT[8] | {...} | Decimal | Bits=1 Corresponding output tracks | Read/Write
raP_Opr_SeqBoolOut | ORdy_bOutput | INT[8] | {...} | Decimal | Bits=1 Corresponding output ready for direct change | Read Only
raP_Opr_SeqBoolOut | Val_MaxBankIndex | DINT | 0 | Decimal | Maximum Bank Index | Read Only
raP_Opr_SeqRealOut | Cfg_bHasOutNav | SINT[4] | {...} | Decimal | Bits=1 indicate inputs with navigation enabled | Read/Write
raP_Opr_SeqRealOut | Cfg_bScaling | SINT[4] | {...} | Decimal | Bits=1 Corresponding output is scaled | Read/Write
raP_Opr_SeqRealOut | Cfg_bTracking | SINT[4] | {...} | Decimal | Bits=1 Corresponding output tracks | Read/Write
raP_Opr_SeqRealOut | ORdy_bOutput | SINT[4] | {...} | Decimal | Bits=1 Corresponding output ready for direct change | Read Only
raP_Opr_SeqRealOut | Val_MaxBankIndex | DINT | 0 | Decimal | Maximum Bank Index | Read Only
raP_Opr_Unit | CmdSrc | P_COMMAND_SOURCE | {...} |  | Control / Command Source Selection. | Read/Write
raP_Opr_Unit | HMI_BusObjIndex | DINT | 0 | Decimal | HMI bus object index. | Read Only
raP_Opr_Unit | MCmd_Acq | BOOL | 0 | Decimal | Maintenance command to acquire ownership (Operator/Program/External/Override to Maintenance). The instruction clears this operand automatically. | Read/Write
raP_Opr_Unit | MCmd_Bypass | BOOL | 0 | Decimal | Maintenance command to bypass all bypassable interlocks and permissives. The instruction clears this operand automatically. | Read/Write
raP_Opr_Unit | MCmd_Check | BOOL | 0 | Decimal | Maintenance command to check (not bypass) all interlocks and permissives. The instruction clears this operand automatically. | Read/Write
raP_Opr_Unit | MCmd_IS | BOOL | 0 | Decimal | Maintenance command to select in service. The instruction clears this operand automatically. | Read/Write
raP_Opr_Unit | MCmd_OoS | BOOL | 0 | Decimal | Maintenance command to select out of service. The instruction clears this operand automatically. | Read/Write
raP_Opr_Unit | MCmd_Physical | BOOL | 0 | Decimal | Maintenance command to select Physical device operation (not virtualized). | Read/Write
raP_Opr_Unit | MCmd_Rel | BOOL | 0 | Decimal | Maintenance command to release ownership (Maintenance to Operator/Program/External/Override). The instruction clears this operand automatically. | Read/Write
raP_Opr_Unit | MCmd_Virtual | BOOL | 0 | Decimal | Maintenance command to select Virtual (virtualized) device operation. | Read/Write
raP_Opr_Unit | MRdy_Acq | BOOL | 0 | Decimal | 1 = Ready for MCmd_Acq, enable HMI button. | Read Only
raP_Opr_Unit | MRdy_Bypass | BOOL | 0 | Decimal | 1 = Ready for MCmd_Bypass, enable HMI button.. | Read Only
raP_Opr_Unit | MRdy_Check | BOOL | 0 | Decimal | 1 = Ready for MCmd_Check, enable HMI button. | Read Only
raP_Opr_Unit | MRdy_IS | BOOL | 0 | Decimal | 1 = Ready for MCmd_IS, enable HMI button. | Read Only
raP_Opr_Unit | MRdy_OoS | BOOL | 0 | Decimal | 1 = Ready for MCmd_OoS, enable HMI button. | Read Only
raP_Opr_Unit | MRdy_Physical | BOOL | 0 | Decimal | 1 = Ready for MCmd_Physical, enable HMI button. | Read Only
raP_Opr_Unit | MRdy_Rel | BOOL | 0 | Decimal | 1 = Ready for MCmd_Rel, enable HMI button. | Read Only
raP_Opr_Unit | MRdy_Virtual | BOOL | 0 | Decimal | 1 = Ready for MCmd_Virtual, enable HMI button. | Read Only
raP_Opr_Unit | OCmd | SINT | 2#0000_0000 | Binary | Operator command to State. (x) The instruction clears this operand automatically. | Read/Write
raP_Opr_Unit | OCmd_Lock | BOOL | 0 | Decimal | Operator command to lock Operator (disallow Program). The instruction clears this operand automatically. | Read/Write
raP_Opr_Unit | OCmd_Normal | BOOL | 0 | Decimal | Operator command to select Normal (Operator or Program). The instruction clears this operand automatically. | Read/Write
raP_Opr_Unit | OCmd_Oper | BOOL | 0 | Decimal | Operator command to select Operator (Program to Operator). The instruction clears this operand automatically. | Read/Write
raP_Opr_Unit | OCmd_OwnerAcq | BOOL | 0 | Decimal | Operator command to acquire child command source. | Read/Write
raP_Opr_Unit | OCmd_OwnerRel | BOOL | 0 | Decimal | Operator command to release child command source. | Read/Write
raP_Opr_Unit | OCmd_ParCapture | DINT | 0 | Decimal | Operator command to capture initial parameter. The instruction clears this operand automatically. Bit: 1 - Param 1 - 16, 2 - Param 17 - 32, 3 - Param 33 - 48, 31 - Param 481 - 496. | Read/Write
raP_Opr_Unit | OCmd_ParClear | DINT | 0 | Decimal | Operator command to clear parameter. The instruction clears this operand automatically. Bit: 1 - Param 1 - 16, 2 - Param 17 - 32, 3 - Param 33 - 48, 31 - Param 481 - 496. | Read/Write
raP_Opr_Unit | OCmd_ParRestore | DINT | 0 | Decimal | Operator command to restore initial parameter. The instruction clears this operand automatically.Bit: 1 - Param 1 - 16, 2 - Param 17 - 32, 3 - Param 33 - 48, 31 - Param 481 - 496. | Read/Write
raP_Opr_Unit | OCmd_Prog | BOOL | 0 | Decimal | Operator command to select Program (Operator to Program). The instruction clears this operand automatically. | Read/Write
raP_Opr_Unit | OCmd_Reset | BOOL | 0 | Decimal | Operator command to reset all alarms request. The instruction clears this operand automatically. | Read/Write
raP_Opr_Unit | OCmd_ResetAckAll | BOOL | 0 | Decimal | Operator command to reset and acknowledge all alarms. The instruction clears this operand automatically. | Read/Write
raP_Opr_Unit | OCmd_RptCapture | DINT | 0 | Decimal | Operator command to capture initial report. The instruction clears this operand automatically. Bit: 1 - Rpt 1 - 16, 2 - Rpt 17 - 32, 3 - Rpt 33 - 48, 31 - Rpt 481 - 496. | Read/Write
raP_Opr_Unit | OCmd_RptClear | DINT | 0 | Decimal | Operator command to clear report. The instruction clears this operand automatically. Bit: 1 - Rpt 1 - 16, 2 - Rpt 17 - 32, 3 - Rpt 33 - 48, 31 - Rpt 481 - 496. | Read/Write
raP_Opr_Unit | OCmd_RptRestore | DINT | 0 | Decimal | Operator command to restore initial report. The instruction clears this operand automatically. Bit: 1 - Rpt 1 - 16, 2 - Rpt 17 - 32, 3 - Rpt 33 - 48, 31 - Rpt 481 - 496. | Read/Write
raP_Opr_Unit | OCmd_Unlock | BOOL | 0 | Decimal | Operator command to unlock or release (allow Program to acquire) ownership. The instruction clears this operand automatically. | Read/Write
raP_Opr_Unit | ORdy | SINT | 2#0000_0000 | Binary | 1 = Ready for OCmd_(x), enable HMI button. | Read Only
raP_Opr_Unit | ORdy_Lock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Lock, enable HMI button. | Read Only
raP_Opr_Unit | ORdy_Normal | BOOL | 0 | Decimal | 1 = Ready for OCmd_Normal, enable HMI button. | Read Only
raP_Opr_Unit | ORdy_Oper | BOOL | 0 | Decimal | 1 = Ready for OCmd_Oper, enable HMI button. | Read Only
raP_Opr_Unit | ORdy_OwnerAcq | BOOL | 0 | Decimal | 1 = Ready for OCmd_OwnerAcq, enable HMI button. | Read Only
raP_Opr_Unit | ORdy_OwnerRel | BOOL | 0 | Decimal | 1 = Ready for OCmd_OwnerRel, enable HMI button. | Read Only
raP_Opr_Unit | ORdy_ParCapture | BOOL | 0 | Decimal | 1 = Ready for OCmd_ParCapture, enable HMI button. | Read Only
raP_Opr_Unit | ORdy_ParClear | BOOL | 0 | Decimal | 1 = Ready for OCmd_ParClear, enable HMI button. | Read Only
raP_Opr_Unit | ORdy_ParRestore | BOOL | 0 | Decimal | 1 = Ready for OCmd_ParRestore, enable HMI button. | Read Only
raP_Opr_Unit | ORdy_Prog | BOOL | 0 | Decimal | 1 = Ready for OCmd_Prog, enable HMI button. | Read Only
raP_Opr_Unit | ORdy_Reset | BOOL | 0 | Decimal | 1 = Ready for OCmd_Reset, enable HMI button. | Read Only
raP_Opr_Unit | ORdy_ResetAckAll | BOOL | 0 | Decimal | 1 = Ready for OCmd_ResetAckAll, enable HMI button. | Read Only
raP_Opr_Unit | ORdy_RptCapture | BOOL | 0 | Decimal | 1 = Ready for OCmd_RptCapture, enable HMI button. | Read Only
raP_Opr_Unit | ORdy_RptClear | BOOL | 0 | Decimal | 1 = Ready for OCmd_RptClear, enable HMI button. | Read Only
raP_Opr_Unit | ORdy_RptRestore | BOOL | 0 | Decimal | 1 = Ready for OCmd_RptRestore, enable HMI button. | Read Only
raP_Opr_Unit | ORdy_Unlock | BOOL | 0 | Decimal | 1 = Ready for OCmd_Unlock, enable HMI button. | Read Only
raP_Opr_VSM | Cfg_MaxCmdIndex | SINT | 31 | Decimal | Max Index for Commands | Read Only
raP_Opr_VSM | Cfg_MaxStateIndex | SINT | 31 | Decimal | Max Index for States | Read Only
raP_Tec_EventQLoad | scr | DINT | 0 | Decimal | Working Scratch | Read/Write
raP_Tec_EventQLoad | Time | DINT[7] | {...} | Decimal | Time used in processing current record | Read/Write
raP_Tec_EventQUnload | ContSerNum | DINT | 0 | Decimal | Serial number of controller | Read/Write
raP_Tec_EventQUnload | Wrk_TypeDefault | STRING_16 | '' |  | Default Type constant | Read/Write
raP_Tec_EventQUnload | xxx_ptr_Read_Old | DINT | -1 | Decimal | Last Scan read pointer | Read/Write
raP_Tec_HARTChanData_to_PAH | None
raP_Tec_LgxEvent | None
raP_Tec_ParRpt | Cfg_Default_E | DINT | 0 | Decimal | Default enumeration parameter value, loaded when Inp_Clear = 1. | Read/Write
raP_Tec_ParRpt | Cfg_Default_I | DINT | 0 | Decimal | Default integer parameter value, loaded when Inp_Clear = 1. | Read/Write
raP_Tec_ParRpt | Cfg_Default_R | REAL | 0 | Float | Default real parameter value, loaded when Inp_Clear = 1. | Read/Write
raP_Tec_ParRpt | Cfg_Default_S | STRING_32 | '' |  | Default string parameter value, loaded when Inp_Clear = 1. | Read/Write
raP_Tec_ParRpt | Cfg_SecurityCode | STRING_16 | 'E' |  | Process area for security. | Read/Write
raP_Tec_ParRpt | ORdy_Adjst | BOOL | 0 | Decimal | Allow adjustment of setting from HMI. 1 = Cfg_ReadWrite = 1 and Inp_Oper = 1 and (Limit operator adjustment limit = 0 Or (Limit operator adjustment = 1 and operator adjustment positive limit NEQ = and operator adjustment negative limit NEQ 0). | Read Only
raP_Tec_ParRpt | OSet_E | DINT | 0 | Decimal | Operator issued setting of enumeration parameter value. | Read/Write
raP_Tec_ParRpt | OSet_I | DINT | 0 | Decimal | Operator issued setting of integer parameter value. | Read/Write
raP_Tec_ParRpt | OSet_R | REAL | 0 | Float | Operator issued setting of real parameter value. | Read/Write
raP_Tec_ParRpt | OSet_S | STRING_32 | '' |  | Operator issued setting of string parameter value. | Read/Write
raP_Tec_ParRpt | Val_Initial_S_Display | STRING_32 | '' |  | Initial string parameter value, while Inp_Trgr = 1, Val_Initial is set to the string parameter setpoint. | Read Only
raP_Tec_SeqCore | none
raP_Tec_SeqEdit | none

## @Library Extended Tag Values
.@Library
System Release | 5 | 5 | 5 | 5.1 | 5.1 | 5.2 | 5.2 | 5.3 | 5.3 | 5.3 | 5.3 | 5.4 | 5.3
Process Library | 5.00.00 | 5.00.01 | 5.00.02 | 5.00.04 | 5.00.06 | 5.10.00 | 5.10.01 | 5.20.00 | 5.20.01 | 5.20.02 | 5.20.03 | 5.30.00 | 5.20.04
Logix Designer | v33 | v33 | v33 | v34 | v34 | v35 | v35 | v36 | v37 | v37 | v37 | v38 | v37
PCMDSRC | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
PAH | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PAI | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PAID | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PAIM | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PAO | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PBL | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PD4SD | --- | --- | --- | --- | --- | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PDBC | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PDI | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PDO | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PDOSE | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PFO | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PHLS | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PINTLK | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PLLS | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PMTR | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PNPOS | --- | --- | --- | --- | --- | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PPERM | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PPID | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PPTC | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PRI | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PRT | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PTST | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PVLV | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PVLVS | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PVLVMP | --- | --- | --- | --- | --- | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
PVSD | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_D4SD | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | --- | --- | --- | --- | --- | --- | --- | ---
raP_Dvc_nPos | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | --- | --- | --- | --- | --- | --- | --- | ---
raP_Dvc_VlvMP | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | --- | --- | --- | --- | --- | --- | --- | ---
raP_Dvc_LgxChangeDet | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_LgxCPU_5x80 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_LgxModuleSts | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_LgxRedun | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_LgxTaskMon | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Opr_ArbitrationQ | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | ---
raP_Opr_Area | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Opr_EMGen | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Opr_EPGen | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Opr_ExtddAlm | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Opr_OrgScan | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Opr_OrgView | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Opr_Owner | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Opr_Prompt | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Opr_Prompt_Core | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Opr_Seq | --- | --- | --- | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Opr_SeqBoolInp | --- | --- | --- | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Opr_SeqBoolOut | --- | --- | --- | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Opr_SeqRealOut | --- | --- | --- | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Opr_Unit | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Opr_VSM | --- | --- | --- | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Tec_EventQLoad | --- | --- | --- | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Tec_EventQUnload | --- | --- | --- | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Tec_HARTChanData_to_PAH | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Tec_LgxEvent | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Tec_ParRpt | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Tec_SeqCore | --- | --- | --- | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Tec_SeqEdit | --- | --- | --- | raP-5_00 | raP-5_00 | raP-5_10 | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_AP_FFLink | --- | --- | --- | --- | --- | --- | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_AP_PALink | --- | --- | --- | --- | --- | --- | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_EN2FFR | --- | --- | --- | --- | --- | --- | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_EN2PAR | --- | --- | --- | --- | --- | --- | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_EH_Flowmeter | --- | --- | --- | --- | --- | --- | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_EH_Sensor | --- | --- | --- | --- | --- | --- | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_EH_Heartbeat | --- | --- | --- | --- | --- | --- | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_EH_Promag53_FW1 | --- | --- | --- | --- | --- | --- | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_EH_Promag100_FW2 | --- | --- | --- | --- | --- | --- | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_EH_Promag300_500 | --- | --- | --- | --- | --- | --- | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_EH_Promag400_FW3 | --- | --- | --- | --- | --- | --- | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_EH_Promag400_V02_Rev4 | --- | --- | --- | --- | --- | --- | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_EH_Promass83_FW2 | --- | --- | --- | --- | --- | --- | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_EH_Promass100_FW3 | --- | --- | --- | --- | --- | --- | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20
raP_Dvc_EH_Promass300_500 | --- | --- | --- | --- | --- | --- | raP-5_10 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_20 | raP-5_30 | raP-5_20

## Summary of Changes
Summary of Changes
| Date | Changes
A | June 2022 | First release as an Excel spreadsheet
B | January 2023 | Updated for 5.10
C | December 2023 | Updated for 5.10.01
D | June 2024 | Updated for 5.20.00
E | March 2025 | Updated for 5.20.01, 5.20.02, 5.00.06
F | October 2025 | Updated for 5.20.03 (Only Extended Tag Value Info)
G | December 2025 | Updated for 5.30.00 (Added Library Extended Tag Values for 5.30.00, Added Cfg_IdleStateNum to raP_Opr_VSM Input Paramters, and added Val_ReturnStateNum to raP_Opr_EMGen Output Parameters)
H | May 2026 | Updated for 5.20.04 (Added Local Tags for P-instructions and Library Extended Tag Values)