## Rev History
iXC2-Core Modbus Register Mapping
Document History:
Doc Version | Date | Description
1.01 | 2015-03-18 | 1. Initial Draft
1.02 | 2015-04-20 | 1. Added ISaGRAF statistics parameters at IR 8151. 2. Reserved IR 8183 - 8200 for ISaGraf.
1.03 | 2015-07-01 | Class Messaging type
1.04 | 2015-08-12 | Modified Mapping template to show following: CP, UDT, Tag Name, COMM type, Storage, On Demand, Access, UOM, Data Min, Data Max, Default
1.05 | 2015-08-27 | Added data on all the above added fields and review
1.06 | 2015-09-24 | 1. Reserved HR:8218 - Reserved for internal use only. 2. Reserved HR:8530 - Reserved for internal use only.
1.07 | 2015-11-27 | 01. Added CS 8036 to Enable / Disable MB Data Copier 02. Added CS 8099 to Reload configuration of MB Data Copier 03. Updated Remarks for CS 8100 - Time Synchronization 04. Updated Remarks for CS 8111 to 12 - Whether to store Default at Power ON for Analog Output 05. Updated Remarks for CS 8117 to 24 - Whether to store Default at Power ON for Digital Output 06. Updated Remarks for CS 8125 to 32 -Default at Power ON for Digital Output 07. Updated Tag Name, Description, No.of Registers for IS 8064 - AI Channels Fault Status 08. Reserved IS 8072 & 73 AI Channels Fault Status for Channel 9 & 10 09. Updated Remarks for IR 8013 - Board Serial Number 10. Added IR 8136 - Halt status of MB Data Copier 11. Updated the Remarks for IR 8151 to 82 - ISaGRAF Status 12. Added IR 8281- 8282 for Version No. of MB Data Copier 13. Added IR 8316 for IO Board Hardware Revision number 14. Updated Tag Name, Description and Remarks for IR 8410 - Pulse ACC, Pulse Per Minute data or Frequency for DI1 to DI9 to include Pulse Per Minute Data. 15. Updated Description and Remarks for IR 8437 to 53 - Analog Input Channels (AI1 to AI8) value in V/mA. 16. Reserved IR 8453 to 56 - Analog Input Channels value in V/mA for AI 9 & 10. 17. Updated the Remarks for IR 8641 to 48 - Lattitude / Longitude. 18. Updated Range and Remarks for HR 8001, HR 8004 to 35, HR 8101 to 04. 19. Added HR 8045 for Status of MB Data Copier. 20. Updated Range for HR 8201 to 02- Analog Output Channel 1 & 2 Raw Count 21. Updated Range for HR 8223 to 26 - Minimum / Maximum Raw for AI Channel and HR 8427 to 30 - Calib Low / High for AI Channel. 22. Updated Description, Range and Remarks for HR 8343 & 44 - Digital Output Latching Interval 23. Added HR 8351 to 58 - Digital Output Type for DO1 to DO8 24. Updated Description, No. of Register Range and Remark for HR 8383 to 90 25. Added HR 8391 & 92 for AI Channel 9 & 10 Input Type 26. Updated Description, No. of Register Range and Remark for HR 8393 to 8400 27. Added HR 8401 for DI Channel 9 Input Type 28. Update Range and Remarks for HR 8402 & 03 -Analog Output Type, HR 8426 - Analog Input Channel Calibration Type 29. Updated Range and Remarks for HR 8472 to 80 - AI input Range selection 30. Updated Range and Remarks for HR 8482 & 83 - Default AO1 & 2 value at Power ON 31. Updated Range and Remarks for HR 8525 to 28 - Set EU Value for AO 1 & 2 32. Updated Range and Remarks for HR 8531 to 39 - DI Status Debouncing Interval 33. Updated Range and Remarks for HR 8542 to 45 - Percent value of AO 34. Updated Range and Remarks for HR 8546 to 49 - Default Set EU Value for AO 35. Updated Range and Remarks for HR 8550 to 53- Default Percent value of AO 36. Updated Range and Remarks for HR 8701, 8751, 8752, 8801 for TCP_Slave, RTU_Master, TCP_Master, RTU_Slave statistic reset 37. Updated Remarks for HR 8851 to 8878 - Message Logger Configuration 38. Added HR 8888 for MB Data Copier Message Logger Configuration 39. Updated Range and Default Value for HR 8231-34- Engineering Unit Low/High Limit
1.08 | February 8 ,2016 | 01. Added CS 8022 to Enable/Disable DNP3 Slave module 02. Added IR 8253 - 8254 for version number of DNP3 Slave module 03. Added IR 8122 for Halt Status of DNP3 Slave module 04. Added HR 8031 for status of DNP3 slave module. 05. Added HR 8874 for Message Log of DNP3 Slave module. 06. Added CS 8023 to Enable/Disable DNP3 Master module. 07. Added IR 8255 - 8256 for version number of DNP3 Master module. 08. Added IR 8123 for Halt Status of DNP3 Master module. 09. Added HR 8032 for status of DNP3 Master module. 10. Added HR 8875 for Message Log of DNP3 Master module. 11. Added CS 8028 to Enable/Disable Enron MB Slave module. 12. Added IR 8265 - 8266 for version number of Enron MB Slave module. 13. Added IR 8128 for Halt Status of Enron MB Slave module. 14. Added HR 8037 for status of Enron MB Slave module. 15. Added HR 8880 for Message Log of Enron MB Slave module. 16. Added CS 8032 to Enable/Disable Ethernet IP module. 17. Added IR 8273 - 8274 for version number of Ethernet IP module. 18. Added IR 8132 for Halt Status o fEthernet IP module. 19. Added HR 8041 for status of Ethernet IP module. 20. Added HR 8884 for Message Log of Ethernet IP module.
1.09 | February 10 ,2016 | 01. Added IR 8016 to 8018 for LAN2 MAC Address. 02. .Added IR 8019 to 8026 for LAN1/LAN2 IP Address.
1.1 | February 22 ,2016 | 01. Added HR 8554 - 8562 for Enable AI scale upto 22mA.
1.11 | April 07 ,2016 | Renamed HR 18351 - 18598 HR 18951 - 18961 IR 30816 - 30823 IR 38122 IR 38136 IR 38256 IR 38281 IR 38316 IR 38410 - 38428 HR 48045 HR 48888
1.12 | April 22 ,2016 | 01. Update all IsaGRAF IR registers to Class 1. 02. Add Comm type to IR Suite parameters.
1.13 | May 05 ,2016 | 01. Tag name updates in Yellow. 02. Previous highlited changes removed.
1.14 | 2016-09-08 | 01. Added Black Oil Model related registers in HR 10001 - 11422
1.15 | 2016-10-06 | 01. Added MQTT Client related registers in CS 8038, IR 8138, IR 8285, HR 8047 and HR 8890
1.16 | 2017-04-11 | 01. Added Gas Flow Measurement Registers 02. Added Gas Flow Measurement Alarm and Events 03. Added IR 8183 - 8190 for ISaGRAF Application Versions for Resource 1 - 4 04. Added AGA related registers in CS 8019, IR 8119, IR 8247, HR 8028 and HR 8871 05. Modified the Description and Remarks for IR 8153 Resource 1 ISaGRAF Application Build Version 06. Added HR 8191 - 8200 for ISaGRAF Registers 07. Removed the Default value from the Range Column
1.17 | 2017-06-02 | 01. Added MQTT Client B related registers in CS 8039, IR 8139, IR 8287, HR 8048 and HR 8891 02. Modified the Tagname and Description for MQTT Client related registers in CS 8038, IR 8138, IR 8285, HR 8047 and HR 8890
1.18 | 2017-06-16 | 01. Modified the No of Registers, Data Type for IR 8154 Cycle Count and Overrun for ISaGRAF Resource 1 02. Modified the Modbus address, No of Registers, Data Type for IR 8158 Overrun for ISaGRAF Resource 1 03. Modified the Modbus address, No of Registers, Remarks for IR 8159 Resource 2 ISaGRAF info 04. Modified the Modbus address, No of Registers, Remarks for IR 8167 Resource 3 ISaGRAF info 05. Modified the Modbus address, No of Registers, Remarks for IR 8175 Resource 4 ISaGRAF info 06. Modified the Modbus address of IR 8183 - 8190 Application Version of Resource 1 - 4 07. Modified the Remarks of HR 17, Meter Identifier. 08. Modified the Remarks of HR 23, Company Name. 09. Modified the Remarks of HR 31, Location.
1.19 | June 19,2017 | 01. Added HR 8691 for Clear Data Logger Files 02. Added HR 8692 for USB Manual Trigger 03. Added IR 8671 for USB Backup Status 04. Added IR 8672 for Data Logger Status 05. Added IR 8673 for Flash Size available
1.2 | July 25,2017 | 01. Added HR 53 for AGA3 inputs DO Unit. 02. Added HR 54 for AGA3 DM Engeenering Unit. 03. Added HR 55 for Density Engineering Unit. 04. Reserved CS 17, Flow Removed Enable/Disable. 05. Reserved IS 14, Alarm Status for Flow Removed. 06. Modified the Tagname of IS 8, High Alarm for DP. 07. Modified the Tagname of IS 9, High Alarm for Density. 08. Modified the Tagname of IS 10, High Alarm for Water Cut. 09. Modified the Tagname of IS 13, Alarm for Flow Cut Off. 10. Modified the Tagname of IS 3,Low Alarm for DP. 11. Modified the Tagname of IS 5,Low Alarm for Water Cut. 12. Added Event Codes 99 - 131 for Gas Flow Measurement.c 13. Reserved CS 16, Flow Cut Off Enable/Disable
1.21 | August 27,2017 | 01. Modified the Gas Flow Measurement Event Codes. It will start from 201.
1.22 | August 31,2017 | 01.Added HR:58 for Reset Historical Reports. 02. Added Event Code 324 for Reset Historical Reports. 03. Added IR 6351- 6361 for Gas Flow Event Report. 04. Added HR 56 for Update Event. 05. Modified the Range, Remarks and Data Max for HR 49, Hourly Report Selection 06. Modified the Range, Remarks and Data Max for HR 50, Daily Report Selection 07. Added IR 8027 - 8028 for Previous time before Time change Event 08. Added IR 8029 - 8030 for Time at which Time was changed
1.23 | 2018-02-08 | 01. Added ISaGRAF_Error sheet 02. Updated Remarks of IR 8152 Resource 1 ISaGRAF Status 03. Modified the DataType of IR 8152 Resource 1 ISaGRAF Status to SHORT from USHORT
1.24 | 2018-04-11 | 01. Added HR 10020 for Tubing Head Pressure Modbus Range Specifier 02. Added HR 10022 for Tubing Head Temperature Modbus Range Specifier 03. Modified the DataType of HR 10019 THP Address from SHORT to USHORT 04. Modified the DataType of HR 10021 THT Address from SHORT to USHORT 05. Modified the DataType of HR 10014 BOM Engine Operation Counter from SHORT to USHORT
1.25 | 2018-06-06 | 01. Added HR 8105 for Time Zone Index 02. Added Timezone sheet 03. Modified the Range and Data Max for HR 8004 Time Zone UTC – Offset in minutes
1.26 | 2018-09-10 | 01. Added Wet Gas Detection Registers in CS 8015, IR 8115 , IR 8239 - 8240 , HR 8024 and HR 8867 02. Added Wet Gas Detection CS 10501 and 10502 03. Added Wet Gas Detection Output in IR 12001 - 12036 04. Added Wet Gas Detection Configuration in HR 14201 - 14282
1.27 | 2018-10-04 | 01. Added License Manager Registers in CS 8040, IR 8140 , IR 8289 - 8290 , HR 8049 and HR 8892
1.28 | 2018-10-12 | 01. Added Ranges and Default values for BOM Registers 02. Marked HR 10195 - 10196 Flashing Temperature Gradient as Reserved 03. Marked HR 10199 Has Assays Database changed as Reserved 04. Marked HR 10200 Assays Database new number as Reserved
1.29 | 2018-11-14 | 01. Marked HR 10465 - 10520, 10565 - 10600, 10421 - 10440, 10341 - 10360, 10253 - 10280 as Reserved 02. Modified the Range and Datamax for HR 10205 - 10208 C1 Bubble Point (BPSC) 03. Modifiedthe Range, DataMin and Default values for HR 11303 - 11352 Flow Measurement Point
1.3 | 2018-11-18 | 01. Modified the Rematks of IR 8152 Status of Resource 1 02. Added HR 8191 - 8194 to enable/disable Resource 1 - 4 03. Added CS 8251 - 8254 to trigger Resource 1 - 4
1.31 | 2019-01-10 | 01. Added HR 8693 Data Logger Data Point Number 02. Added HR 8694 Data Logger Parameter Number 03. Added HR 8695 - 8696 Data Logger Parameter Value 04. Added IR 8674 - 8675 Data Logger Read Parameter Value 05. Added IR 8676 Data Logger Read Write Status 06. Added CS 8351 Trigger Write Parameter 07. Aded CS 8352 Trigger Read Parameter
1.32 | 2019-03-25 | 01. Modified the Default Value of HR 14201 - 14202 Algorithm Trigger Time 02. Modified the Default Value of HR 14203 - 14204 MB Scan Time 03. Modified the Default Value of HR 14233 - 14234 Partial Pressure H2O Correlation [APPH2O] 04. Modified the Default Value of HR 14257 - 14258 Cond Molecular Weight Linear Regression [CCMW] 05. Modified the DataMin, DataMax and Default value for CS 10501 Algorithm Select 06. Modified the DataMin, DataMax and Default value for CS 10502 EU Inverse
1.33 | May 02 ,2019 | 01. Modified the Range, DataMax and Remarks for HR 8693 Data Point Number 02. Modified the Range, DataMax and Remarks for HR 8694 Parameter Number 03. Modified the Remarks for HR 8695 Parameter Value 04. Modified the Remarks for IR 8674 Read Parameter Value 05. Modified the Range, Remarks for IR 8676 Data Logger Read/Write Status 06. Modified the Remarks for CS 8351 Trigger Write Parameter 07. Modified the Remarks for CS 8352 Trigger Read Parameter 08. Modified the Remarks for HR 8191 - 8194 Enable/Disable ISaGRAF Resource
1.34 | July 08 ,2019 | 01. Added Provisioning Registers in CS 8041, IR 8141 , IR 8291 - 8292 , HR 8050 and HR 8893

## Modbus ID
#No | Parameter | Default Modbus ID
1 | RTU Modbus ID | 1
2 | WMP Modbus ID | 235

## iXC2-CS
CP | Tag Name | MODBUS CS | Description | No. of Registers | Range | Comm Type | Data type | Remarks | Storage | On Demand | Access | UOM | Data Min | Data Max | Default
Gas Flow Measurement
| AGA3Enbl | 1 | AGA3 Enable/Disable | 1 | 0 or 1 | O1 | Bit | 0 = Disable AGA3. 1 = Enable AGA3. If AGA3 is enabled then it will do the AGA3 Calculation | NV |  | R/W |  | 0 | 1 | 1
| AGA7Enbl | 2 | AGA7/9 Enable/Disable | 1 | 0 or 1 | O1 | Bit | 0 = Disable the AGA 7/9. 1 = Enable the AGA 7/9. Whether AGA 7 or 9 will run is decided by HR 10. | NV |  | R/W |  | 0 | 1 | 0
| MaintMd | 3 | Maintenance Mode | 1 | 0 or 1 | O1 | Bit | 0 = Turn Off Maintenance Mode. 1 = Turn On Maintenance Mode | NV |  | R/W |  | 0 | 1 | 0
| PFLoAlmEnbl | 4 | Flowing Pressure Low Alarm Enable / Disable | 1 | 0 or 1 | O1 | Bit | Flowing Pressure Low Alarm Enable / Disable 0 = Disable 1 = Enable | NV |  | R/W |  | 0 | 1 | 1
| PFHiAlmEnbl | 5 | Flowing Pressure High Alarm Enable / Disable | 1 | 0 or 1 | O1 | Bit | Flowing Pressure High Alarm Enable / Disable 0 = Disable 1 = Enable | NV |  | R/W |  | 0 | 1 | 1
| TFLoAlmEnbl | 6 | Flowing Temperature Low Alarm Enable / Disable | 1 | 0 or 1 | O1 | Bit | Flowing Temperature Low Alarm Enable / Disable 0 = Disable 1 = Enable | NV |  | R/W |  | 0 | 1 | 1
| TFHiAlmEnbl | 7 | Flowing Temperature High Alarm Enable / Disable | 1 | 0 or 1 | O1 | Bit | Flowing Temperature High Alarm Enable / Disable 0 = Disable 1 = Enable | NV |  | R/W |  | 0 | 1 | 1
| DiffPLoAlmEnbl | 8 | Differential Pressure Low Alarm Enable / Disable | 1 | 0 or 1 | O1 | Bit | Differential Pressure Low Alarm Enable / Disable 0 = Disable 1 = Enable | NV |  | R/W |  | 0 | 1 | 1
| DiffPHiAlmEnbl | 9 | Differential Pressure High Alarm Enable / Disable | 1 | 0 or 1 | O1 | Bit | Differential Pressure High Alarm Enable / Disable 0 = Disable 1 = Enable | NV |  | R/W |  | 0 | 1 | 1
| DensLoAlmEnbl | 10 | Density Low Alarm Enable / Disable | 1 | 0 or 1 | O1 | Bit | Density Low Alarm Enable / Disable 0 = Disable 1 = Enable | NV |  | R/W |  | 0 | 1 | 1
| DensHiAlmEnbl | 11 | Density High Alarm Enable / Disable | 1 | 0 or 1 | O1 | Bit | Density High Alarm Enable / Disable 0 = Disable 1 = Enable | NV |  | R/W |  | 0 | 1 | 1
| WCtLoAlmEnbl | 12 | Water Cut Low Alarm Enable / Disable | 1 | 0 or 1 | O1 | Bit | Water Cut Low Alarm Enable / Disable 0 = Disable 1 = Enable | NV |  | R/W |  | 0 | 1 | 1
| WCtHiAlmEnbl | 13 | Water Cut High Alarm Enable / Disable | 1 | 0 or 1 | O1 | Bit | Water Cut High Alarm Enable / Disable 0 = Disable 1 = Enable | NV |  | R/W |  | 0 | 1 | 1
| FLRLoAlmEnbl | 14 | Flow Rate Low Alarm Enable / Disable | 1 | 0 or 1 | O1 | Bit | Flow Rate Low Alarm Enable / Disable 0 = Disable 1 = Enable | NV |  | R/W |  | 0 | 1 | 1
| FLRHiAlmEnbl | 15 | Flow Rate High Alarm Enable / Disable | 1 | 0 or 1 | O1 | Bit | Flow Rate High Alarm Enable / Disable 0 = Disable 1 = Enable | NV |  | R/W |  | 0 | 1 | 1
|  | 16 | Reserved for Flow Computer | 85
|  | 101 | Reserved for Applications | 7900
RTU Kernel
| EnblRTUKernel | 8001 | Enable RTU Kernel | 1 |  | C3 | Bit | Writing 0 to this will reboot the system | NV | No | R/W | - | - | - | 1
| EnblMsgLgr | 8002 | Enable Message Logger | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 1
| EnblAlmMngr | 8003 | Enable Alarm Manager | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 0
| EnblDtLgr | 8004 | Enable Data Logger | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 0
| EnblIODtAcqtn | 8005 | Enable IO_DataAcquisition | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 1
| EnblMBRTUMstr | 8006 | Enable MB RTU Master | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 0
| EnblMBRTUSlv | 8007 | Enable MB RTU Slave | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 0
| EnblMBTCPMstr | 8008 | Enable MB TCP Master | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 0
| EnblMBTCPSlv | 8009 | Enable MB TCP Slave | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 1
|  | 8010 | Reserved for Debug | 4 |  |  | Bit
| EnblWebSvr | 8014 | Enable Web Server | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 1
| EnblWetGDtctn | 8015 | Enable Wet Gas Detection | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 0
|  | 8016 | Reserved for Debug | 1 |  |  | Bit
| EnblISaGRAF | 8017 | Enable ISaGRAF | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 0
|  | 8018 | Reserved for Debug | 1 |  |  | Bit
| EnblAGA | 8019 | Enable AGA | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 0
|  | 8020 | Reserved for Debug | 2
| EnblDNP3Slv | 8022 | Enable DNP3 Slave | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 0
| EnblDNP3Mstr | 8023 | Enable DNP3 Master | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 0
|  | 8024 | Reserved for Debug | 2
| EnblWMP | 8026 | Enable WMP | 1 | 0 or 1 | C3 |  | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 1
|  | 8027 | Reserved for Debug | 1 |  |  | Bit
| EnblEnrbMBSlv | 8028 | Enable Enron MB Slave | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 0
|  | 8029 | Reserved for Debug | 3
| EnblEthIP | 8032 | Enable Ethernet IP | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV | No | R/W | - | - | - | 0
|  | 8033 | Reserved for Debug | 3
| EnblMBDtCpy | 8036 | Enable MB Data Copier | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV |  | R/W | - | - | - | 1
| EnblBOM | 8037 | Enable Black Oil Model | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV |  | R/W | - | - | - | 0
| EnblMQTTCliA | 8038 | Enable MQTT Client A | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV |  | R/W | - | - | - | 0
| EnblMQTTCliB | 8039 | Enable MQTT Client B | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV |  | R/W | - | - | - | 0
| EnblLcnsMngr | 8040 | Enable License Manager | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV |  | R/W | - | - | - | 0
| EnblPrvsng | 8041 | Enable Provisioning | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will enable the module (RTU Kernel will make the module RUN). Writing 0 to this register will disable the module. It also shows the module status. | NV |  | R/W | - | - | - | 0
|  | 8042 | Reserved | 57
| RldCfgMBDtCpy | 8099 | Reload configuration of MB Data Copier | 1 | 0 or 1 | C3 | Bit | Writing 1 to this regisdter will reload configuration of MB Data Copier. (MB Data Copier will work as per new configuration) MB Data Copier module will make this register 0. | NV |  | R/W
| TmSynctn | 8100 | Time Synchronization | 1 | 0 or 1 | C3 | Bit | Time synchronization flag. Writing 1 to this register will set new Board time as per the values updated in HR 8005 - 8010. This is automatically resets to 0 after the process. | NV | No | R/W | - | - | - | -
|  | Input Output | [9 empty] | - | - | - | -
| DO1 | 8101 | Digital Output 1 | 1 | 0 or 1 | O1 | Bit | Writing 1 to this register will enable the DO1. Writing 0 will disabale the DO. | NV | No | R/W | - | - | - | 0
| DO2 | 8102 | Digital Output 2 | 1 | 0 or 1 | O1 | Bit | Writing 1 to this register will enable the DO2. Writing 0 will disabale the DO. | NV | No | R/W | - | - | - | 0
| DO3 | 8103 | Digital Output 3 | 1 | 0 or 1 | O1 | Bit | Writing 1 to this register will enable the DO3. Writing 0 will disabale the DO. | NV | No | R/W | - | - | - | 0
| DO4 | 8104 | Digital Output 4 | 1 | 0 or 1 | O1 | Bit | Writing 1 to this register will enable the DO4. Writing 0 will disabale the DO. | NV | No | R/W | - | - | - | 0
| DO5 | 8105 | Digital Output 5 | 1 | 0 or 1 | O1 | Bit | Writing 1 to this register will enable the DO5. Writing 0 will disabale the DO. | NV | No | R/W | - | - | - | 0
| DO6 | 8106 | Digital Output 6 | 1 | 0 or 1 | O1 | Bit | Writing 1 to this register will enable the DO6. Writing 0 will disabale the DO. | NV | No | R/W | - | - | - | 0
| DO7 | 8107 | Digital Output 7 | 1 | 0 or 1 | O1 | Bit | Writing 1 to this register will enable the DO7. Writing 0 will disabale the DO. | NV | No | R/W | - | - | - | 0
| DO8 | 8108 | Digital Output 8 | 1 | 0 or 1 | O1 | Bit | Writing 1 to this register will enable the DO8. Writing 0 will disabale the DO. | NV | No | R/W | - | - | - | 0
|  | 8109 | Reserved for Debug | 1 |  |  | Bit
|  | 8110 | Reserved for Debug | 1 |  |  | Bit
| AO1DfltPwrup | 8111 | Whether to store Default at Power ON for Analog Output (AO1) | 1 | 0 or 1 | C3 | Bit | Writing 0 to this register will hold the default value at power ON. Writing 1 to this register will set 0 V or 4mA depending upon the AO1 type at Power ON. | NV |  | R/W
| AO2DfltPwrup | 8112 | Whether to store Default at Power ON for Analog Output (AO2) | 1 | 0 or 1 | C3 | Bit | Writing 0 to this register will hold the default value at power ON. Writing 1 to this register will set 0 V or 4 mA depending upon the AO2 type at Power ON. | NV |  | R/W
|  | 8113 | Reserved for Debug | 1 |  |  | Bit
|  | 8114 | Reserved for Debug | 3 |  |  | Bit
| DO1DfltPwrup | 8117 | Whether to store Default at Power ON for Digital Output (DO1) | 1 | 0 or 1 | C3 | Bit | Writing 0 to this register will hold the default value at power ON. Writing 1 to this register will set 0 at DO1. | NV | No | R/W
| DO2DfltPwrup, DO8DfltPwrup | 8118 | Whether to store Default at Power ON for Digital Output (DO2 to DO8) | 7 | 0 or 1 | C3 | Bit | Same as above for DO2 to DO8 | NV | No | R/W
| DO1DfltPwrupVal | 8125 | Default values at Power ON for DO1 depending on the status bit CS:8117 | 1 | 0 or 1 | C3 | Bit | This value will be updated at DO1 if CS 8117 is set 0. | NV | No | R/W
| DO2DfltPwrupVal, DO8DfltPwrupVal | 8126 | Default values at Power ON for DO2 to DO7 depending on the status bit CS:8118 to 8124 | 7 | 0 or 1 | C3 | Bit | Same as above for DO2 to DO8 dpending on the status of CS:8118 to 8124 respectively. | NV | No | R/W
| AICh1and2EnblSnglDiff | 8133 | AI Channel-1 & 2 set as single differential | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will set Analog Input Channel 1 & 2 to read Differential Input Signal | NV | No | R/W
| AICh3and4EnblSnglDiff | 8134 | AI Channel-3 & 4 set as single differential | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will set Analog Input Channel 3 & 4 to read Differential Input Signal | NV | No | R/W
| AICh5and6EnblSnglDiff | 8135 | AI Channel-5 & 6 set as single differential | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will set Analog Input Channel 5 & 6 to read Differential Input Signal | NV | No | R/W
| AICh7and8EnblSnglDiff | 8136 | AI Channel-7 & 8 set as single differential | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will set Analog Input Channel 7 & 8 to read Differential Input Signal | NV | No | R/W
|  | 8137 | Reserved | 4 |  |  | Bit
| D01HiLoInvsnSeltn | 8141 | DO1 level (High / Low) inversion selection. | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will invert the DO1. | NV | No | R/W | - | - | - | -
| D02HiLoInvsnSeltn, D08HiLoInvsnSeltn | 8142 | Similar as 8141, for DO2 to D08, respectively. | 7 | 0 or 1 | C3 | Bit | Same as above for DO2 to DO8 | NV | No | R/W | - | - | - | -
|  | 8149 | Reserved | 2
MB RTU Master
|  | 8151 | Reserved for Debug | 1 |  |  | Bit
|  | 8152 | Reserved for Debug | 1 |  |  | Bit
|  | 8153 | Reserved for Debug | 1 |  |  | Bit
|  | 8154 | Reserved for Debug | 1 |  |  | Bit
|  | 8155 | Reserved | 46
Alarm Manager
| ReStngAlmStsAICh1 | 8201 | Resetting Alarm status for Analog Input channel 1 | 1 | 0 or 1 | C3 | Bit | Writing 1 to this register will reset the Alarm status for AI 1 | NV | No | R/W | - | - | - | -
| ReStngAlmStsAICh2, ReStngAlmStsAICh10 | 8202 | Resetting Alarm status for Analog Input channel 2 to 10 | 9 | 0 or 1 | C3 | Bit | Same as above for AI 2 to AI 10 | NV | No | R/W | - | - | - | -
|  | 8211 | Reserved | 40 |  |  | Bit
ISaGRAF
| TrgrRes1 | 8251 | Trigger Resource 1 | 1 | 0 or 1 | C3 | Bit | Writing 1 to tis register will trigger the Start/Stop/Restart of Resource 1 updated in HR 8191. ISaGRAF will reset it to 0 once the operation is done | NV | No | R/W |  | 0 | 1 | 0
| TrgrRes2 | 8252 | Trigger Resource 2 | 1 | 0 or 1 | C3 | Bit | Writing 1 to tis register will trigger the Start/Stop/Restart of Resource 2 updated in HR 8192. ISaGRAF will reset it to 0 once the operation is done | NV | No | R/W |  | 0 | 1 | 0
| TrgrRes3 | 8253 | Trigger Resource 3 | 1 | 0 or 1 | C3 | Bit | Writing 1 to tis register will trigger the Start/Stop/Restart of Resource 3 updated in HR 8193. ISaGRAF will reset it to 0 once the operation is done | NV | No | R/W |  | 0 | 1 | 0
| TrgrRes4 | 8254 | Trigger Resource 4 | 1 | 0 or 1 | C3 | Bit | Writing 1 to tis register will trigger the Start/Stop/Restart of Resource 4 updated in HR 8194. ISaGRAF will reset it to 0 once the operation is done | NV | No | R/W |  | 0 | 1 | 0
|  | 8255 | Reserved | 96 |  |  | Bit
Data Logger
| TrgrWritePrmtr | 8351 | Trigger Write Parameter | 1 | 0 or 1 | C3 | Bit | Writing 1 to tis register will trigger the parameter value updated in HR 8695 - 8696 to be written to the Data Point/Common Data and Parameter Number mentioned in HR 8693 and HR 8694 respectively.Data Logger will reset it to 0 once the operation is done | NV | No | R/W |  | 0 | 1 | 0
| TrgrReadPrmtr | 8352 | Trigger Read Parameter | 1 | 0 or 1 | C3 | Bit | Writing 1 to tis register will trigger the parameter value to be updated in IR 8674 - 8675 for the Data Point/Common Data and Parameter Number mentioned in HR 8693 and HR 8694 respectively.Data Logger will reset it to 0 once the operation is done | NV | No | R/W |  | 0 | 1 | 0
|  | 8353 | Reserved | 648 |  |  | Bit
3rd Party Slave
|  | 9001 | Reserved for 3rd Party Slave | 1000 |  |  | Bit
|  | 10001 | Reserved for iNOC | 500 |  |  | Bit
Wet Gas Detection
| AlgoSelt | 10501 | Algorithm Select | 1 | 0 or 1 | C3 | Bit | Select Algorithm 0 - Revision A 1 - Revision B | NV | No | R/W | - | 0 | 1 | 1
| EUInvs | 10502 | EU Inverse | 1 | 0 or 1 | C3 | Bit | Select Algorithm 0 - Not Inverse 1 - Inverse | NV | No | R/W | - | 0 | 1 | 0
|  | 10503 | Reserved | 98 |  |  | Bit

## iXC2-IS
CP | Tag Name | MODBUS IS | Description | No. of Registers | Range | Comm Type | Data type | Remarks | Storage | On Demand | Access | UOM | Data Min | Data Max | Default
Gas Flow Measurement
| LoAlmPF | 10001 | Low Alarm for PF | 1 | 0 or 1 | I1 | bit | Low Alarm for Flowing Pressure in Local/Remote Mode | NV |  | R
| LoAlmTF | 10002 | Low Alarm for TF | 1 | 0 or 1 | I1 | bit | Low Alarm for Flowing Temperature in Local/Remote Mode | NV |  | R
| LoAlmDiffP | 10003 | Low Alarm for DP | 1 | 0 or 1 | I1 | bit | Low Alarm for Differential Pressure in Local/Remote Mode | NV |  | R
| LoAlmDens | 10004 | Low Alarm for Density | 1 | 0 or 1 | I1 | bit | Low Alarm for Density in Local/Remote Mode | NV |  | R
| LoAlmWCt | 10005 | Low Alarm for Water Cut | 1 | 0 or 1 | I1 | bit | Low Alarm for Water Cut in Local/Remote Mode | NV |  | R
| HiAlmPF | 10006 | High Alarm for PF | 1 | 0 or 1 | I1 | bit | High Alarm for Flowing Pressure in Local/Remote Mode | NV |  | R
| HiAlmTF | 10007 | High Alarm for TF | 1 | 0 or 1 | I1 | bit | High Alarm for Flowing Temperature in Local/Remote Mode | NV |  | R
| HiAlmDiffP | 10008 | High Alarm for DP | 1 | 0 or 1 | I1 | bit | High Alarm for Differential Pressure in Local/Remote Mode | NV |  | R
| HiAlmDens | 10009 | High Alarm for Density | 1 | 0 or 1 | I1 | bit | High Alarm for Density in Local/Remote Mode | NV |  | R
| HiAlmWCt | 10010 | High Alarm for Water Cut | 1 | 0 or 1 | I1 | bit | High Alarm for Water Cut in Local/Remote Mode | NV |  | R
| LoAlmFLR | 10011 | Low Alarm for Flow Rate | 1 | 0 or 1 | I1 | bit | Low Alarm for Flow Rate | NV |  | R
| HiAlmFLR | 10012 | High Alarm for Flow Rate | 1 | 0 or 1 | I1 | bit | High Alarm for Flow Rate | NV |  | R
| AlmFLCtOff | 10013 | Alarm for Flow Cut Off | 1 | 0 or 1 | I1 | bit | Flow Cut Off Alarm | NV |  | R
|  | 10014 | Reserved for Flow Computer | 987 |  |  | Bit
| AppltnSpec | 11001 | Reserved for Applications | 7000 | - |  | Bit
RTU Kernel
|  | 18001 | Reserved for Debug | 1
|  | 18002 | Reserved | 49
Input Output
| DI1 | 18051 | Digital Input 1 | 1 | - | I1 | BIT | Digital Input Channel 1 Status | NV | No | R | - | - | - | -
| DI2, DI9 | 18052 | Digital Input 2 to 9 | 8 | - | I1 | BIT | Same as above for Channel 2 to 9 | NV | No | R | - | - | - | -
|  | 18060 | Reserved for Debug | 3
| WtchDogResetSts | 18063 | Watchdog Reset Status | 1 | 0 or 1 | I1 |  | If 1, Last reset occurred due to watchdog reset. | NV | No | R | - | - | - | -
| AICh1FltSts, AICh8FltSts | 18064 | AI Channels Fault Status, for AI1 to AI8 | 8 | 0 or 1 | I1 | BIT | If 1, that AI channel shows FAULT status, else it is normal. | NV | No | R | - | - | - | -
|  | 18072 | Reserved | 29
MB RTU Master
| NdActvFlgSlvID1 | 18101 | Node Active Flag for Slave ID 1 | 1 | - | I3 | BIT | If a Third Party Slave with ID 1 is connected in the network, this is set to 1 otherwise 0 | NV | No | R | - | - | - | -
| NdActvFlgSlvID2, NdActvFlgSlvID247 | 18102 | Node Active Flag for Slave ID 2 -247 | 246 | - | I3 | BIT | Same as above for 3rd Party Slave ID 2 to 247 | NV | No | R | - | - | - | -
|  | 18348 | Reserved | 3
| ThirdPartySlvPrtclFlgSlvID1 | 18351 | Third Party Slave protocol Flag for Slave ID 1 | 1 | - | I3 | BIT | If a Third Party Slave with ID 1 is connected in network it displays the communication protocol between RTU and the slave. If it is RTU then it is set to 1. In case of ASCII, it is set to 0. | NV | No | R | - | - | - | -
| ThirdPartySlvPrtclFlgSlvID2, ThirdPartySlvPrtclFlgSlvID247 | 18352 | Third Party Slave protocol Flag for Slave ID 2 - 247 | 246 | - | I3 | BIT | Same as above for 3rd Party Slave ID 2 to 247 | NV | No | R | - | - | - | -
|  | 18598 | Reserved | 3
| SerLnkStsSlvID1 | 18601 | Serial Link Status for Slave ID 1 | 1 | - | I3 | BIT | It shows the status of the communication between RTU and 3rd Party Slave ID 1. If they are communicating it is set to 1 otherwise 0. | NV | No | R | - | - | - | -
| SerLnkStsSlvID2, SerLnkStsSlvID247 | 18602 | Serial Link Status for Slave ID 2 - 247 | 246 | - | I3 | BIT | Same as above for 3rd Party Slave ID 2 to 247 | NV | No | R | - | - | - | -
|  | 18848 | Reserved | 103
Alarm Manager
| AlmAICh1Sts | 18951 | Alarm status for Analog Input channel 1 | 1 | - | I1 | BIT |  | NV | No | R | - | - | - | -
| AlmAICh2Sts, AlmAICh10Sts | 18952 | Alarm status for Analog Input channels 2 to 10 | 9 | - | I1 | BIT |  | NV | No | R | - | - | - | -
|  | 18961 | Reserved | 40
3rd Party Manager
|  | 19001 | Reserved for 3rd Party devices | 1000

## iXC2-IR
CP | Tag Name | MODBUS IR | Description | No of Registers | Range | Comm Type | Data type | Remarks | Storage | On Demand | Access | UOM | Data Min | Data Max | Default
| AppltnSpec | 30001 | Application Specific | 6000
Gas Flow Measurement
| AGA8OutErrCd | 36001 | AGA8 OUTPUT ERROR CODE | 1 |  | I3 | SHORT | AGA8 OUTPUT ERROR CODE | NV | No | R
| AGA3OutERRCd | 36002 | AGA3 OUTPUT ERROR CODE | 1 |  | I3 | SHORT | AGA3 OUTPUT ERROR CODE | NV | No | R
| AGA7OutERRCd | 36003 | AGA7/9 OUTPUT ERROR CODE | 1 |  | I3 | SHORT | AGA7/9 OUTPUT ERROR CODE | NV | No | R
| AGA3OutCDFLG | 36004 | AGA3 OUTPUT CDFLAG | 1 |  | I3 | SHORT | Orifice plate coefficient of discharge bound flag (CDFLAG) | NV | No | R
| AGA7LMF | 36005 | AGA7 LMF number | 1 |  | I3 | SHORT | AGA7 LMF number | NV | No | R
| AGAInpDP | 36006 | AGA Input DP | 2 |  | I3 | FLOAT | Differential Pressure Input for AGA calculations | NV | No | R
| AGAInpPF | 36008 | AGA Input PF | 2 |  | I3 | FLOAT | Flowing Pressure Input for AGA calculation | NV | No | R
| AGAInpTF | 36010 | AGA Input TF | 2 |  | I3 | FLOAT | Flowing Temperature Input for AGA calculation | NV | No | R
| AGAInpDens | 36012 | AGA Input RHOTP | 2 |  | I3 | FLOAT | Density at flowing condition (RHOTP) | NV | No | R
| AGAInpWCt | 36014 | AGA Input Water Cut | 2 |  | I3 | FLOAT | AGA Input Water Cut | NV | No | R
| AGAInpPulses | 36016 | AGA Input Pulses | 2 |  | I3 | FLOAT | AGA Input Pulses | NV | No | R
| AGA8OutTS | 36018 | AGA8 OUTPUT TS | 2 |  | I3 | FLOAT | Standard Temperature (TS) | NV | No | R
| AGA8OutPS | 36020 | AGA8 OUTPUT PS | 2 |  | I3 | FLOAT | Standard Pressure (PS) | NV | No | R
| AGA8OutZF | 36022 | AGA8 OUTPUT ZF | 2 |  | I3 | FLOAT | Compressibility Factor at Flowing condition (ZF) | NV | No | R
| AGA8OutZB | 36024 | AGA8 OUTPUT ZB | 2 |  | I3 | FLOAT | Compressibility Factor at Base condition (ZB) | NV | No | R
| AGA8OutZS | 36026 | AGA8 OUTPUT ZS | 2 |  | I3 | FLOAT | Compressibility Factor at Standard condition (ZS) | NV | No | R
| AGA8OutRHOTP | 36028 | AGA8 OUTPUT RHOTP | 2 |  | I3 | FLOAT | Density at flowing condition (RHOTP) | NV | No | R
| AGA8OutRHOB | 36030 | AGA8 OUTPUT RHOB | 2 |  | I3 | FLOAT | Density at base condition (RHOB) | NV | No | R
| AGA8OutRHOS | 36032 | AGA8 OUTPUT RHOS | 2 |  | I3 | FLOAT | Density at standard condition (RHOS) | NV | No | R
| AGA8OutFPVS | 36034 | AGA8 OUTPUT FPVS | 2 |  | I3 | FLOAT | Super Compressibility factor (FPVS) | NV | No | R
| AGA8OutMWGAS | 36036 | AGA8 OUTPUT MWGAS | 2 |  | I3 | FLOAT | Molecular weight of gas (MWGAS) | NV | No | R
| AGA8OutGRB | 36038 | AGA8 OUTPUT GRB | 2 |  | I3 | FLOAT | Specific gravity at base condition (GRB) | NV | No | R
| AGA8OutGRS | 36040 | AGA8 OUTPUT GRS | 2 |  | I3 | FLOAT | Specific gravity at standard condition (GRS) | NV | No | R
| AGA3OutQV | 36042 | AGA3 OUTPUT QV | 2 |  | I3 | FLOAT | Volume flow rate at standard condition (QV) | NV | No | R
| AGA3OutDOC | 36044 | AGA3 OUTPUT DOC | 2 |  | I3 | FLOAT | Temperature corrected orifice diameter (DOC) | NV | No | R
| AGA3OutDMC | 36046 | AGA3 OUTPUT DMC | 2 |  | I3 | FLOAT | Temperature corrected pipe diameter (DMC) | NV | No | R
| AGA3OutEV | 36048 | AGA3 OUTPUT EV | 2 |  | I3 | FLOAT | Velocity of approach factor (EV) | NV | No | R
| AGA3OutCD | 36050 | AGA3 OUTPUT CD | 2 |  | I3 | FLOAT | Orifice Plate coefficient of discharge (CD) | NV | No | R
| AGA3OutFN | 36052 | AGA3 OUTPUT FN | 2 |  | I3 | FLOAT | Numeric conversion factor (FN) | NV | No | R
| AGA3OutFC | 36054 | AGA3 OUTPUT FC | 2 |  | I3 | FLOAT | Orifice calculation factor (FC) | NV | No | R
| AGA3OutFSL | 36056 | AGA3 OUTPUT FSL | 2 |  | I3 | FLOAT | Orifice slope factor (FSL) | NV | No | R
| AGA3OutFA | 36058 | AGA3 OUTPUT FA | 2 |  | I3 | FLOAT | Pipe tap orifice expansion factor(FA) | NV | No | R
| AGA3OutCPRM | 36060 | AGA3 OUTPUT CPRM | 2 |  | I3 | FLOAT | Pipe tap orifice flow constant (CPRM) | NV | No | R
| AGA3OutY | 36062 | AGA3 OUTPUT Y | 2 |  | I3 | FLOAT | Expansion Factor (Y) | NV | No | R
| AGA3OutFB | 36064 | AGA3 OUTPUT FB | 2 |  | I3 | FLOAT | Basic orifice factor (FB) | NV | No | R
| AGA3OutFR | 36066 | AGA3 OUTPUT FR | 2 |  | I3 | FLOAT | Reynold number factor (FR) | NV | No | R
| AGA3OutFPB | 36068 | AGA3 OUTPUT FPB | 2 |  | I3 | FLOAT | Base pressure factor (FPB) | NV | No | R
| AGA3OutFTB | 36070 | AGA3 OUTPUT FTB | 2 |  | I3 | FLOAT | Base temperature factor (FTB) | NV | No | R
| AGA3OutFTF | 36072 | AGA3 OUTPUT FTF | 2 |  | I3 | FLOAT | Flowing temperature factor (FTF) | NV | No | R
| AGA3OutFGR | 36074 | AGA3 OUTPUT FGR | 2 |  | I3 | FLOAT | Relative density (FGR) | NV | No | R
| AGA3OutAVGEL | 36076 | AGA3 OUTPUT AVGVEL | 2 |  | I3 | FLOAT | Average fluid velocity in pipe (AVGVEL) | NV | No | R
| AGA3OutRED | 36078 | AGA3 OUTPUT RED | 2 |  | I3 | FLOAT | Reynolds number (RED) | NV | No | R
| AGA3OutBETA | 36080 | AGA3 OUTPUT BETA | 2 |  | I3 | FLOAT | Beta Ratio (BETA) | NV | No | R
| AGA3DrvROutQM | 36082 | AGA3 OUTPUT QM | 2 |  | I3 | FLOAT | Mass Flow Rate (QM) | NV | No | R
| AGA3DrvROutQB | 36084 | AGA3 OUTPUT QB | 2 |  | I3 | FLOAT | Volumetric flow rate at base condition (QB) | NV | No | R
| AGA3OutDrvrOutQFF | 36086 | AGA3 OUTPUT QFF | 2 |  | I3 | FLOAT | Volumetric flow rate using flange factor meter (QFF) | NV | No | R
| AGA3OutCFP | 36088 | AGA3 OUTPUT CFP | 2 |  | I3 | FLOAT | Composite orifice factor C' for flange taps (CFP) | NV | No | R
| AGA3OutCPP | 36090 | AGA3 OUTPUT CPP | 2 |  | I3 | FLOAT | Orifice factor for pipe taps (CPP) | NV | No | R
| AGA7QF | 36092 | AGA7 OUTPUT QF | 2 |  | I3 | FLOAT | Flow Rate at flow condition (QF) | NV | No | R
| AGA7VF | 36094 | AGA7 OUTPUT VF | 2 |  | I3 | FLOAT | Volume at flowing condition (VF) | NV | No | R
| AGA7VS | 36096 | AGA7 OUTPUT VS | 2 |  | I3 | FLOAT | Volume at standard condition (VS) | NV | No | R
| AGA7MF | 36098 | AGA7 OUTPUT MF * LMF | 2 |  | I3 | FLOAT | Total applied factor for (MF * LMF ) | NV | No | R
| CDiffP | 36100 | Current Differential Pressure/Pulses | 2 |  | I3 | FLOAT | Current Differential Pressure/Pulses | NV | No | R
| CP | 36102 | Current Pressure | 2 |  | I3 | FLOAT | Current Pressure | NV | No | R
| CTemp | 36104 | Current Temperature | 2 |  | I3 | FLOAT | Current Temperature | NV | No | R
| CDens | 36106 | Current Density | 2 |  | I3 | FLOAT | Current Density | NV | No | R
| CDiffPExtn | 36108 | Current Differential Pressure Extension/Pulse Accumulation | 2 |  | I3 | FLOAT | Current Differential Pressure Extension/Pulse Accumulation | NV | No | R
| CWCt | 36110 | Current water Cut. | 2 |  | I3 | FLOAT | Current water Cut. | NV | No | R
| CCPrime | 36112 | Current C Prime | 2 |  | I3 | FLOAT | Current C Prime | NV | No | R
| DiffPHrly | 36114 | Differential Pressure Hourly/Pulse Hourly | 2 |  | I3 | FLOAT | Differential Pressure Hourly/Pulse Hourly | NV | No | R
| PHrly | 36116 | Pressure Hourly | 2 |  | I3 | FLOAT | Pressure Hourly | NV | No | R
| TempHrly | 36118 | Temperature Hourly | 2 |  | I3 | FLOAT | Temperature Hourly | NV | No | R
| DensHrly | 36120 | Density Hourly | 2 |  | I3 | FLOAT | Density Hourly | NV | No | R
| DiffPExtnHrly | 36122 | Differential Pressure Extension Hourly/Pulse Accumulation Hourly | 2 |  | I3 | FLOAT | Differential Pressure Extension Hourly/Pulse Accumulation Hourly | NV | No | R
| WCtHrly | 36124 | Water Cut Hourly | 2 |  | I3 | FLOAT | Water Cut Hourly | NV | No | R
| CPrimeHrly | 36126 | C Prime Hourly | 2 |  | I3 | FLOAT | C Prime Hourly | NV | No | R
| CMassFLR | 36128 | Current Mass Flow rate | 2 |  | I3 | FLOAT | Current Mass Flow rate | NV | No | R
| CNetTotVol | 36130 | Current Net total volume | 2 |  | I3 | FLOAT | Current Net total volume | NV | No | R
| CGrsTotVol | 36132 | Current Gross Total Volume | 2 |  | I3 | FLOAT | Current Gross Total Volume | NV | No | R
| CEnrgyTotVol | 36134 | Current Energy Total Volume | 2 |  | I3 | FLOAT | Current Energy Total Volume | NV | No | R
| FLTmHrly | 36136 | Flow Time in Seconds Hourly | 2 |  | I3 | FLOAT | Flow Time in Seconds Hourly | NV | No | R
| CMassFLRHrly | 36138 | Current Mass Flow rate Hourly | 2 |  | I3 | FLOAT | Hourly Mass Flow Rate | NV | No | R
| CNetTotVolHrly | 36140 | Current Net total volume Hourly | 2 |  | I3 | FLOAT | Hourly Net total volume | NV | No | R
| CGrsTotVolHrly | 36142 | Current Gross Total Volume Hourly | 2 |  | I3 | FLOAT | Hourly Gross Total Volume | NV | No | R
| CEnergyTotVolHrly | 36144 | Current Energy Total Volume Hourly | 2 |  | I3 | FLOAT | Hourly Energy Total Volume | NV | No | R
| FLTmDaily | 36146 | Flow Time in Seconds Daily | 2 |  | I3 | FLOAT | Flow Time in Hours Daily | NV | No | R
| CMassFLRDaily | 36148 | Current Mass Flow rate Daily | 2 |  | I3 | FLOAT | Daily Mass Flow Rate | NV | No | R
| CNetTotVolDaily | 36150 | Current Net total volume Daily | 2 |  | I3 | FLOAT | Daily Net total volume | NV | No | R
| CGrsTotVolDaily | 36152 | Current Gross Total Volume Daily | 2 |  | I3 | FLOAT | Daily Gross Total Volume | NV | No | R
| CEnergyTotVolDaily | 36154 | Current Energy Total Volume Daily | 2 |  | I3 | FLOAT | Daily Energy Total Volume | NV | No | R
|  | 36156 | Reserved | 15
|  | 36171 | Reserved for future | 90 | [7 empty] | ̊
Hourly Report
| HrlyRepTmStampDa | 36261 | Time Stamp Day | 1 |  | I3 | USHORT | Time Stamp Day | NV | Yes | R
| HrlyRepTmStampMo | 36262 | Time Stamp Month | 1 |  | I3 | USHORT | Time Stamp Month | NV | Yes | R
| HrlyRepTmStampYr | 36263 | Time Stamp Year | 1 |  | I3 | USHORT | Time Stamp Year | NV | Yes | R
| HrlyRepTmStampHr | 36264 | Time Stamp Hour | 1 |  | I3 | USHORT | Time Stamp Hour | NV | Yes | R
| HrlyRepTmStampMin | 36265 | Time Stamp Minutes | 1 |  | I3 | USHORT | Time Stamp Minutes | NV | Yes | R
| HrlyRepTmStampSec | 36266 | Time Stamp Seconds | 1 |  | I3 | USHORT | Time Stamp Seconds | NV | Yes | R
| HrlyRepFLTm | 36267 | Flow Time in Seconds | 2 |  | I3 | Float | Flow Time in Seconds.This Reg shows current Flow time in seconds. It resets to zero after Hourly report is saved | NV | Yes | R
| HrlyRepNetTotVol | 36269 | Net total volume | 2 |  | I3 | Float | Net total volume | NV | Yes | R
| HrlyRepGrsTotVol | 36271 | Gross Total Volume | 2 |  | I3 | Float | Gross Total Volume | NV | Yes | R
| HrlyRepAveDiffP | 36273 | Averaged Differential Pressure/Pulses | 2 |  | I3 | Float | Averaged Differential Pressure/Pulses | NV | Yes | R
| HrlyRepAveP | 36275 | Average pressure | 2 |  | I3 | Float | Average pressure | NV | Yes | R
| HrlyRepAveTemp | 36277 | Average temperature | 2 |  | I3 | Float | Average temperature | NV | Yes | R
| HrlyRepAveDens | 36279 | Average Density (RHOTP) | 2 |  | I3 | Float | Average Density (RHOTP) | NV | Yes | R
| HrlyRepAveDiffPExtn | 36281 | Average Diff-Pressure Extension/Pulse Accumulation | 2 |  | I3 | Float | Average Diff-Pressure Extension/Pulse Accumulation | NV | Yes | R
| HrlyRepAveCPrime | 36283 | Average C Prime | 2 |  | I3 | Float | Average C Prime | NV | Yes | R
|  | 36285 | Reserved for future Hourly Report Data | 16
Daily Report
| DailyRepTmStampDa | 36301 | Time Stamp Day | 1 |  | I3 | USHORT | Time Stamp Day | NV | Yes | R
| DailyRepTmStampMo | 36302 | Time Stamp Month | 1 |  | I3 | USHORT | Time Stamp Month | NV | Yes | R
| DailyRepTmStampYr | 36303 | Time Stamp Year | 1 |  | I3 | USHORT | Time Stamp Year | NV | Yes | R
| DailyRepTmStampHr | 36304 | Time Stamp Hour | 1 |  | I3 | USHORT | Time Stamp Hour | NV | Yes | R
| DailyRepTmStampMin | 36305 | Time Stamp Minutes | 1 |  | I3 | USHORT | Time Stamp Minutes | NV | Yes | R
| DailyRepTmStampSec | 36306 | Time Stamp Seconds | 1 |  | I3 | USHORT | Time Stamp Seconds | NV | Yes | R
| DailyRepFLTm | 36307 | Flow Time in hours | 2 |  | I3 | Float | Flow Time in hours | NV | Yes | R
| DailyRepGrsTotVol | 36309 | Gross Total Volume | 2 |  | I3 | Float | Gross Total Volume | NV | Yes | R
| DailyRepNetTotVol | 36311 | Net total volume | 2 |  | I3 | Float | Net total volume | NV | Yes | R
| DailyRepMassTotVol | 36313 | Mass Total volume | 2 |  | I3 | Float | Mass Total volume | NV | Yes | R
| DailyRepEnrgyTotVol | 36315 | Energy Total volume | 2 |  | I3 | Float | Energy Total volume | NV | Yes | R
| DailyRepAveDiffP / DailyRepAvePulse | 36317 | Average Diff-Pressure /Pulses | 2 |  | I3 | Float | Average Diff-Pressure /Pulses | NV | Yes | R
| DailyRepAveP | 36319 | Average pressure | 2 |  | I3 | Float | Average pressure | NV | Yes | R
| DailyRepAveTemp | 36321 | Average temperature | 2 |  | I3 | Float | Average temperature | NV | Yes | R
| DailyRepAveDens | 36323 | Average Density (RHOTP) | 2 |  | I3 | Float | Average Density (RHOTP) | NV | Yes | R
| DailyRepAveDiffPExtn | 36325 | Average Diff-Pressure Extension /Pulse Accumulation | 2 |  | I3 | Float | Average Diff-Pressure Extension /Pulse Accumulation | NV | Yes | R
| DailyRepAveWCt | 36327 | Average water Cut or BS & W. | 2 |  | I3 | Float | Average water Cut or BS & W. | NV | Yes | R
| DailyRepAveCPrime | 36329 | Average C Prime | 2 |  | I3 | Float | Average C Prime | NV | Yes | R
|  | 36331 | Reserved for future Daily Report Data | 20 | [7 empty] | ̊
Event Report
| EvtRepTmStampDa | 36351 | Time Stamp Day | 1 |  | I3 | USHORT | Time Stamp Day | NV | Yes | R | ̊
| EvtRepTmStampMo | 36352 | Time Stamp Month | 1 |  | I3 | USHORT | Time Stamp Month | NV | Yes | R
| EvtRepTmStampYr | 36353 | Time Stamp Year | 1 |  | I3 | USHORT | Time Stamp Year | NV | Yes | R
| EvtRepTmStampHr | 36354 | Time Stamp Hour | 1 |  | I3 | USHORT | Time Stamp Hour | NV | Yes | R
| EvtRepTmStampMin | 36355 | Time Stamp Minutes | 1 |  | I3 | USHORT | Time Stamp Minutes | NV | Yes | R
| EvtRepTmStampSec | 36356 | Time Stamp Seconds | 1 |  | I3 | USHORT | Time Stamp Seconds | NV | Yes | R
| EvtRepEventCode | 36357 | Event Code | 1 |  | I3 | USHORT | Reported Event Code | NV | Yes | R
| EvtRepOldVal | 36358 | Old Value | 2 |  | I3 | Float | Old Value | NV | Yes | R
| EvtRepNewVal | 36360 | New Value | 2 |  | I3 | Float | New Value | NV | Yes | R
|  | 36362 | Reserved for Flow Computer | 39 | [7 empty] | ̊
|  | 36401 | Reserved for Applications | 1600
RTU Kernel
| BrdTm | 38001 | Board Time (UTC) | 2 | - | I3 | LONG | Current Board Time | NV | No | R | UTC Seconds | - | - | -
| BrdStartTm | 38003 | Board Start Time (UTC) | 2 | - | I3 | LONG | RTU starting time | NV | No | R | UTC Seconds | - | - | -
|  | 38005 | Reserved | 2
| LocTm.Mo | 38007 | Local Time – Month | 1 | - | I1 | USHORT | Current Time. | NV | No | R | MM | - | - | -
| LocTm.Da | 38008 | Local Time – Day | 1 | - | I1 | USHORT |  | NV | No | R | DD | - | - | -
| LocTm.Yr | 38009 | Local Time – Year | 1 | - | I1 | USHORT |  | NV | No | R | YY | - | - | -
| LocTm.Hr | 38010 | Local Time – Hour | 1 | - | I1 | USHORT |  | NV | No | R | Hr | - | - | -
| LocTm.Mins | 38011 | Local Time – Minutes | 1 | - | I1 | USHORT |  | NV | No | R | Min | - | - | -
| LocTm.Secs | 38012 | Local Time – Seconds | 1 | - | I1 | USHORT |  | NV | No | R | Sec | - | - | -
| BrdSerNum | 38013 | Board Serial Number | 3 | - | I3 | USHORT | LAN 1 MAC address is used as serial number. Lower byte of IR 8013 contains lower byte of MAC Address and in same mannerhigher byte of IR 8015 contains higher byte (6 the byte) of MAC Address. Each register contains 2 bytes of the MAC address and shows the decimal equivalent of the same. | NV | No | R | - | - | - | -
| Lan2MacAd | 38016 | LAN 2 MAC address | 3 |  | I3 | USHORT | LAN 2 MAC address. Lower byte of IR 8016 contains lower byte of MAC Address and in same manner higher byte of IR 8018 contains higher byte (6 the byte) of MAC Address.Each register contains 2 bytes of the MAC address and shows the decimal equivalent of the same. | NV | No | R | -
| Lan1IPAd | 38019 | LAN1 IP Address | 4 |  | I3 | USHORT | LAN1 IP Address | NV | No | R | -
| Lan2IPAd | 38023 | LAN2 IP Address | 4 |  | I3 | USHORT | LAN2 IP Address | NV | No | R | -
| PrevTmChgTmEvt | 38027 | Previous time before Time change Event | 2 |  | I3 | ULONG | Previous time before Time change | NV | No | R | Sec
| TmChgEvtTm | 38029 | Time at which Time was changed | 2 |  | I3 | ULONG | Time at which Time was changed | NV | No | R | Sec
|  | 38031 | Reserved | 70
| HaltStsRTUKernel | 38101 | Halt status of RTU Kernel | 1 |  | I3 | SHORT | 0 - Not Applicable 1 - Fault | NV | No | R | -
| HaltStsMsgLgr | 38102 | Halt status of Message Logger | 1 |  | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | -
| HaltStsAlmMngr | 38103 | Halt Status of Alarm Manager | 1 |  | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R
| HaltStsDtLgr | 38104 | Halt status of Data Logger | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
| HaltStsIODtAcqtn | 38105 | Halt status of IO_DataAcquisition | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
| HaltStsMBRTUMstr | 38106 | Halt status of MB RTU Master | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
| HaltStsMBRTUSlv | 38107 | Halt status of MB RTU Slave | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
| HaltStsMBTCPMstr | 38108 | Halt status of MB TCP Master | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
| HaltStsMBTCPSlv | 38109 | Halt status of MB TCP Slave | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
|  | 38110 | Reserved for Debug | 4 |  |  | SHORT
| HaltStsWebSvr | 38114 | Halt status of Web Server | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
| HaltStsWetGDtctn | 38115 | Halt status of Wet Gas Detection | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
|  | 38116 | Reserved for Debug | 1 |  |  | SHORT
| HaltStsISaGRAF | 38117 | Halt status of IsaGRAF | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
|  | 38118 | Reserved for Debug | 1 |  |  | SHORT
| HaltStsAGA | 38119 | Halt status of AGA | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
|  | 38120 | Reserved for Debug | 2 |  |  | SHORT
| HaltStsDNP3Slv | 38122 | Halt status of DNP3 Slave | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
| HaltStsDNP3Mstr | 38123 | Halt status of DNP3 Master | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
|  | 38124 | Reserved for Debug | 2 |  |  | SHORT
| HaltStsWMP | 38126 | Halt status of WMP | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
|  | 38127 | Reserved for Debug | 1 |  |  | SHORT
| HaltStsEnrnMBSlv | 38128 | Halt status of Enron MB Slave | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
|  | 38129 | Reserved for Debug | 3
| HaltStsEthIP | 38132 | Halt status of Ethernet IP | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
|  | 38133 | Reserved for Debug | 3
| HaltStsMBDtCpy | 38136 | Halt status of MB Data Copier | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
| HaltStsBOM | 38137 | Halt status of Black Oil Model | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
| HaltStsMQTTCliA | 38138 | Halt status of MQTT Client A | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
| HaltStsMQTTCliB | 38139 | Halt status of MQTT Client B | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
| HaltStsLcnsMngr | 38140 | Halt status of License Manager | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
| HaltStsPrvsng | 38141 | Halt status of Provisioning | 1 | - | I3 | SHORT | 0 - Not Applicable 1 - Fault 2 - Stopped Manually | NV | No | R | - | - | - | -
|  | 38142 | Reserved | 9
ISaGRAF
| ISaGRAF_Res1.ID | 38151 | Resource1 ISaGRAF ID | 1 | - | I1 | USHORT | Resource identification number which is defined in ISaGRAPH Workbench for Resource 1 | NV | No | R | - | - | - | -
| ISaGRAF_Res1.Sts | 38152 | Resource 1 ISaGRAF Status | 1 | - | I1 | SHORT | Status of Resource 1. 0 = No Application 1 = Stopped 2 = Running 3 = Running, Single Step 4 = Stopped, Fatal Error 5 = Stopped, Fatal Error (DIV0) 6 = Stopped, Fatal Error (BOUND) (For specific error refer to ISaGRAF_Erro Sheet) | NV | No | R | - | - | - | -
| ISaGRAF_Res1.Ver | 38153 | Resource 1 ISaGRAF Application Build Version | 1 | - | I1 | USHORT | Version Number of Resource 1. It increments by 1 when the application gets compiled | NV | No | R | - | - | - | -
| ISaGRAF_Res1.CycCnt | 38154 | Resource 1 ISaGRAF Cycle Count | 2 | - | I1 | ULONG | Total number of cycles Resource 1 runs. | NV | No | R | - | - | - | -
| ISaGRAF_Res1.CCycTm | 38156 | Resource 1 ISaGRAF Current Cycle Time | 1 | - | I1 | USHORT | Time spent by Resource 1 in current cycle | NV | No | R | - | - | - | -
| ISaGRAF_Res1.ProgCycTm | 38157 | Resource 1 ISaGRAF Program Cycle Time | 1 | - | I1 | USHORT | Cycle Time defined in ISaGRAF workbench for Resource 1. | NV | No | R | - | - | - | -
| ISaGRAF_Res1.MaxCycTm | 38158 | Resource 1 ISaGRAF Resource I Max Cycle Time | 1 | - | I1 | USHORT | Maximum time used by Resource 1 to run a cycle. | NV | No | R | - | - | - | -
| ISaGRAF_Res1.OverRun | 38159 | Resource 1 ISaGARF Overrun | 2 | - | I1 | ULONG | Number of times Resource 1's execution time exceeded the Program Time | NV | No | R | - | - | - | -
| ISaGRAF_Res2 | 38161 | Resource 2 ISaGRAF info same as Resource 1 | 10 | - | I1 | USHORT | Same as 8151 - 8160 for Resource 2 | NV | No | R | - | - | - | -
| ISaGRAF_Res3 | 38171 | Resource 3 ISaGRAF info same as Resource 1 | 10 | - | I1 | USHORT | Same as 8151 - 8160 for Resource 3 | NV | No | R | - | - | - | -
| ISaGRAF_Res4 | 38181 | Resource 4 ISaGRAF infor same as Resource 1 | 10 | - | I1 | USHORT | Same as 8151 - 8160 for Resource 4 | NV | No | R | - | - | - | -
| VerNumISaGRAF_Res1 | 38191 | User defined Resource 1 ISaGRAF Application Version | 2 |  | I1 | FLOAT | User defined Resource 1 ISaGRAF Application Version. | NV | No | R
| VerNumISaGRAF_Res2 | 38193 | User defined Resource 2 ISaGRAF Application Version | 2 |  | I1 | FLOAT | User defined Resource 2 ISaGRAF Application Version | NV | No | R
| VerNumISaGRAF_Res3 | 38195 | User defined Resource 3 ISaGRAF Application Version | 2 |  | I1 | FLOAT | User defined Resource 3 ISaGRAF Application Version | NV | No | R
| VerNumISaGRAF_Res4 | 38197 | User defined Resource 4 ISaGRAF Application Version | 2 |  | I1 | FLOAT | User defined Resource 4 ISaGRAF Application Version | NV | No | R
|  | 38199 | Reserved | 2
Version Number
|  | 38201 | Reserved | 2
| SuiteVerMajNum | 38203 | Suite Version Major Number | 1 | - | I3 | USHORT | Major number of the suite version | NV | No | R | - | - | - | -
| SuiteVerMnrNum | 38204 | Suite Version Minor Number | 1 | - | I3 | USHORT | Minor number of the suite version | NV | No | R | - | - | - | -
| SuiteVerHotFixNum | 38205 | Suite Version Hot Fix Number | 1 | - | I3 | USHORT | Hot Fix Number of the suite version | NV | No | R | - | - | - | -
|  | 38206 | Reserved for Internal Use | 1
| VerNumLinuxGhostImg | 38207 | Version No. Linux Ghost Image | 2 | - | I3 | FLOAT | Linux Ghost Image Version Number | NV | No | R | - | - | - | -
| VerNumSuiteFW | 38209 | Version No. Suite Firmware | 2 | - | I3 | FLOAT | Suite Version Number | NV | No | R | - | - | - | -
| VerNumRTUKernel | 38211 | Version No. RTU Kernel | 2 | - | I3 | FLOAT | RTU Kernel Version Number | NV | No | R | - | - | - | -
| VerNumMsgLgr | 38213 | Version No. Message Logger | 2 | - | I3 | FLOAT | Message Logger Version Number | NV | No | R | - | - | - | -
| VerNumAlmMngr | 38215 | Version No. Alarm Manager | 2 | - | I3 | FLOAT | Alarm Manager Version Number | NV | No | R | - | - | - | -
| VerNumDtLgr | 38217 | Version No. Data Logger | 2 | - | I3 | FLOAT | Data Logger Version Number | NV | No | R | - | - | - | -
| VerNumDtAcqtn | 38219 | Version No. IO_DataAcqusition | 2 | - | I3 | FLOAT | I/O Data Acquisition Version Number | NV | No | R | - | - | - | -
| VerNumMBRTUMstr | 38221 | Version No. MB RTU Master | 2 | - | I3 | FLOAT | RTU Master Version Number | NV | No | R | - | - | - | -
| VerNumMBRTUSlv | 38223 | Version No. MB RTU Slave | 2 | - | I3 | FLOAT | RTU Slave Version Number | NV | No | R | - | - | - | -
| VerNumMBTCPMstr | 38225 | Version No. MB TCP Master | 2 | - | I3 | FLOAT | TCP Master Version Number | NV | No | R | - | - | - | -
| VerNumMBTCPSlv | 38227 | Version No. MB TCP Slave | 2 | - | I3 | FLOAT | TCP Slave Version Number | NV | No | R | - | - | - | -
|  | 38229 | Reserved for Debug | 8 |  |  | FLOAT
| VerNumWebSvr | 38237 | Version No. Web Server | 2 | - | I3 | FLOAT | Web Server Version Number | NV | No | R | - | - | - | -
| VerNumWetGDtctn | 38239 | Version No. Wet Gas Detection | 2 | - | I3 | FLOAT | Wet Gas Detection Version Number | NV | No | R | - | - | - | -
|  | 38241 | Reserved for Debug | 2 |  |  | FLOAT
| VerNumISaGRAF | 38243 | Version No. IsaGRAF | 2 | - | I3 | FLOAT | iSAGraf Version Number | NV | No | R | - | - | - | -
|  | 38245 | Reserved for Internal Use | 2
| VerNumAGA | 38247 | Version No. AGA | 2 | - | I3 | FLOAT | AGA Version Number | NV | No | R | - | - | - | -
|  | 38249 | Reserved for Debug | 4 |  |  | FLOAT
| VerNumDNP3Slv | 38253 | Version No. DNP3 Slave | 2 | - | I3 | FLOAT | DNP3 Slave Version Number | NV | No | R | - | - | - | -
| VerNumDNP3Mstr | 38255 | Version No. DNP3 Master | 2 | - | I3 | FLOAT | DNP3 Master Version Number | NV | No | R | - | - | - | -
|  | 38257 | Reserved for Debug | 4
| VerNumWMP | 38261 | Version No. WMP | 2 | - | I3 | FLOAT | WMP Version Number | NV | No | R | - | - | - | -
|  | 38263 | Reserved for Debug | 2 |  |  | FLOAT
| VerNumEnrnMBSlv | 38265 | Version No. Enron MB Slave | 2 | - | I3 | FLOAT | Enron MB Slave Version Number | NV | No | R | - | - | - | -
|  | 38267 | Reserved for Internal Use | 6
| VerNumEthIP | 38273 | Version No. Ethernet IP | 2 | - | I3 | FLOAT | Ethernet IP Version Number | NV | No | R | - | - | - | -
|  | 38275 | Reserved for Internal Use | 6
| VerNumMBDtCpy | 38281 | Version No. MB Data Copier | 2 | - | I3 | FLOAT | MB Data Copier Version Number | NV | No | R | - | - | -
| VerNumBOM | 38283 | Version No. Black Oil Model | 2 | - | I3 | FLOAT | Black Oil Model Version Number | NV | No | R | - | - | -
| VerNumMQTTCliA | 38285 | Version No. MQTT Client A | 2 | - | I3 | FLOAT | MQTT Client A Version Number | NV | No | R | - | - | -
| VerNumMQTTCliB | 38287 | Version No. MQTT Client B | 2 | - | I3 | FLOAT | MQTT Client B Version Number | NV | No | R | - | - | -
| VerNumLcnsMngr | 38289 | Version No. License Manager | 2 | - | I3 | FLOAT | License Manager Version Number | NV | No | R | - | - | - | -
| VerNumPrvsng | 38291 | Version No. Provisioning | 2 | - | I3 | FLOAT | Provisioning Version Number | NV | No | R | - | - | - | -
|  | 38293 | Reserved | 18
Input Output
|  | 38311 | Reserved | 3 |  |  | UINT
| IOBrdFWVerNum | 38314 | IO Board Firmware Version number | 2 | - | I3 | FLOAT | I/O Board f/w Version Number | NV | No | R | - | - | - | -
| IOBrdHWVerNum | 38316 | IO Board Hardware Version number | 1 | - | I3 | HEX | I/O Board h/w Revsion Number | NV | No | R | - | - | - | -
|  | 38317 | Reserved | 13
| RawAICh1,RawAICh10 | 38330 | Raw Data for Input Analog Channel1 to channel 10 (AI1 to AI0) | 20 | - | I3 | ULONG | Raw Count/ ADC Count for Channel 1 to 10 | NV | No | R | - | - | - | -
| EUAICh1, EUAICh10 | 38350 | EU Data for Input Analog Channel1 to channel 10 (AI1 to AI0) | 20 | - | I1 | FLOAT | EU data for Channel 1 to 10. | NV | No | R | - | - | - | -
|  | 38370 | Reserved for Debug | 20 |  |  | FLOAT
|  | 38390 | Reserved for Debug | 20 |  |  | FLOAT
| DI1PulseCntr, DI9PulseCntr | 38410 | Pulse ACC or Frequency for DI1 to DI9 or Pulse Per Minute data for DI9 | 18 | - |  | ULONG | Pulse Accumulation or Frequency for DI Channel 1 to 9 or Pulse Per Minute for DI Channel 9. | NV | No | R | - | - | -
|  | 38428 | Reserved | 3
|  | 38431 | Reserved for Debug | 2 |  |  | ULONG
|  | 38433 | Reserved for Debug | 2 |  |  | ULONG
|  | 38435 | Reserved | 2
| AICh1V, AICh8V | 38437 | Analog Input Channels (AI1 to AI8) value in V/mA. | 16 | - | I3 | FLOAT | Applied input in terms of v/mA for AI 1 to 8 | NV | No | R | V | - | - | -
|  | 38453 | Reserved for Debug | 24 |  |  | FLOAT
|  | 38477 | Reserved for Debug | 20 |  |  | FLOAT
|  | 38497 | Reserved for Debug | 20 |  |  | FLOAT
|  | 38517 | Reserved for Debug | 18 |  |  | ULONG
|  | 38535 | Reserved for Debug | 2 |  |  | ULONG
|  | 38537 | Reserved for Debug | 2 |  |  | ULONG
|  | 38539 | Reserved for Debug | 20 |  |  | FLOAT
|  | 38559 | Reserved for Debug | 20 |  |  | FLOAT
|  | 38579 | Reserved for Debug | 18 |  |  | ULONG
|  | 38597 | Reserved | 44
Web Server
| LatDir | 38641 | Latitude direction 1 = N, -1 = S | 1 | - | I3 | SHORT | Coordinate Data | NV | No | R | - | - | - | -
| LatDeg | 38642 | Latitude Degree | 1 | - | I3 | USHORT |  | NV | No | R | - | - | - | -
| LatMins | 38643 | Latitude Minute | 1 | - | I3 | USHORT |  | NV | No | R | - | - | - | -
| LatSecs | 38644 | Latitude Second | 1 | - | I3 | USHORT |  | NV | No | R | - | - | - | -
| LongDir | 38645 | Longitude direction 1 = E, -1 = W | 1 | - | I3 | SHORT |  | NV | No | R | - | - | - | -
| LongDeg | 38646 | Longitude Degree | 1 | - | I3 | USHORT |  | NV | No | R | - | - | - | -
| LongMins | 38647 | Longitude Minute | 1 | - | I3 | USHORT |  | NV | No | R | - | - | - | -
| LongSecs | 38648 | Longitude Second | 1 | - | I3 | USHORT |  | NV | No | R | - | - | - | -
|  | 38649 | Reserved | 22
Data Logger
| USBBkUpSts | 38671 | USB Backup Status | 1 | 0 to 6 | I3 | USHORT | USB Backup Status 0 - USB not Connected 1 - USB Connected 2 - Backup Successful 3 - Error 4 - Backup in Progress 5 - USB Lib Initialization Failed 6 - No Data to Copy | NV | No | R | - | 0 | 6 | 0
| DtLgrSts | 38672 | Data Logger Status | 1 | 0 to 2 | I3 | USHORT | Data Logger Status 0 - No Error 1 - Disk Full 2 - No Older File to Delete | NV | No | R | - | 0 | 2 | 0
| FlashSzAval | 38673 | Flash Size available | 1 | 0 to 100 | I3 | USHORT | Flash Size availale | NV | No | R | % | 0 | 100 | 0
| ReadPrmtrVal | 38674 | Read Parameter Value | 2 |  | I3 | FLOAT | This is the Parameter value read from the Configuration file. The Data Point/Common Data will be as mentioned in HR 8693 and Parameter Number in HR 8694. | NV | No | R | - |  |  | 0
| DtLgrReadWriteSts | 38676 | Data Logger Read/Write Status | 1 | 0 to 6 | I3 | USHORT | Data Logger Read/Write Status 0 - Default/In Progress 1 - Read Successful 2 - Write Successful 3 - Invalid Data Point Number 4 - Invalid Parameter Number 5 - Out of Range Parameter Value 6 - Disk Full, File Name not Changed | NV | No | R | - | 0 | 5 | 0
|  | 38677 | Reserved | 4
MB TCP Slave
| NumMBTCPCliCnctd | 38681 | Number of Modbus TCP client connected | 1 | - | I3 | SHORT | Number of TCP clients connected currently to the system | NV | No | R | - | - | - | -
|  | 38682 | Reserved | 19
MB Master
|  | 38701 | Reserved for Internal Use | 1 |  |  | USHORT
|  | 38702 | Reserved for Internal Use | 246 |  |  | USHORT
|  | 38948 | Reserved | 3
Alarm Manager
| AICh1AlmVal | 38951 | Alarm Value for Analog Input channel 1 | 2 | - | I3 | FLOAT | Value at which Alarm for Channel 1 for Triggered | NV | No | R | - | - | - | -
| AICh1AlmTm | 38953 | Time of Alarm for Analog Input channel 1 | 2 | - | I3 | ULONG | Unix Time at which Alarm for Channel 1 for Triggered | NV | No | R | - | - | - | -
| AICh1AlmTyp | 38955 | Type of Alarm (1-Low, 2- High) | 1 | - | I3 | USHORT | Type of Alarm | NV | No | R | - | - | - | -
| AICh2AlmVal, AICh10AlmVal AICh2AlmTm, AICh10AlmTm AICh2AlmTyp, AICh10AlmTyp | 38956 | Alarm Value,Time and Type for Analog Input channel 2 to 10 | 45 | - | I3 |  |  | NV | No | R | - | - | - | -
3rd Party Slave
|  | 39001 | Reserved for 3rd Party Slave | 1000
|  | 310001 | Reserved foriNOC | 2000
Wet Gas Detection
| WetGPrdctnR | 312001 | Wet Gas Production Rate | 2 |  | I3 | FLOAT | Wet Gas Production Rate | NV | No | R | e6sm3/d | - | - | -
| DryGPrdctnR | 312003 | Dry Gas Production Rate at STP | 2 |  | I3 | FLOAT | Dry Gas Production Rate | NV | No | R | e6sm3/d | - | - | -
| CndnstPrdctnR | 312005 | Condensate Production Rate at STP | 2 |  | I3 | FLOAT | Condensate Production Rate | NV | No | R | sm3/d | - | - | -
| WPrdctnR | 312007 | Water Production Rate at STP | 2 |  | I3 | FLOAT | Water Production Rate | NV | No | R | sm3/d | - | - | -
| WetGMassFLR | 312009 | Wet Gas Mass Flow Rate | 2 |  | I3 | FLOAT | Wet Gas Mass Flow Rate | NV | No | R | kg/s | - | - | -
| GFroudeNum | 312011 | Gas Froude Number | 2 |  | I3 | FLOAT | Gas Froude Number | NV | No | R | - | - | - | -
| LqdFroudeNum | 312013 | Liquid Froude Number | 2 |  | I3 | FLOAT | Liquid Froude Number | NV | No | R | - | - | - | -
| LockhartMartinelliNum | 312015 | Lockhart Martinelli Number | 2 |  | I3 | FLOAT | Lockhart Martinelli Number | NV | No | R | - | - | - | -
| GPseudoRdcdTempVenturi | 312017 | Gas Pseudo Reduced Temperature at Venturi | 2 |  | I3 | FLOAT | Gas Pseudo Reduced Temperature at Venturi | NV | No | R | K | - | - | -
| GPseudoRdcdPVenturi | 312019 | Gas Pseudo Reduced Pressure at Venturi | 2 |  | I3 | FLOAT | Gas Pseudo Reduced Pressure at Venturi | NV | No | R | Kpa | - | - | -
| GMolclrWtVenturi | 312021 | HC Gas Molecular Weight at Venturi | 2 |  | I3 | FLOAT | HC Gas Molecular Weight at Venturi | NV | No | R | kg/kgmol | - | - | -
| PseudoCrtclPG | 312023 | Pseudo Critical Pressure of Gas | 2 |  | I3 | FLOAT | Pseudo Critical Pressure of Gas | NV | No | R | Kpa | - | - | -
| PseudoCrtclTempG | 312025 | Pseudo Critical Temperature of Gas | 2 |  | I3 | FLOAT | Pseudo Critical Temperature of Gas | NV | No | R | K | - | - | -
| CndnstDensVenturi | 312027 | Condenstate Density at Venturi | 2 |  | I3 | FLOAT | Condenstate Density at Venturi | NV | No | R | kg/m3 | - | - | -
| CndnstMolclrWtVenturi | 312029 | Condenstate Molecular Weight at Venturi | 2 |  | I3 | FLOAT | Condenstate Molecular Weight at Venturi | NV | No | R | kg/kgmol | - | - | -
| CndnstGRatio | 312031 | Condensate Gas Ratio | 2 |  | I3 | FLOAT | Condensate Gas Ratio | NV | No | R | m3/m3 | - | - | -
| LqdWGRatioVenturi | 312033 | Liquid Water Gas Ratio at venturi | 2 |  | I3 | FLOAT | Liquid Water Gas Ratio at venturi | NV | No | R | m3/m3 | - | - | -
| WetGOverreadingFctr | 312035 | Wet Gas Overreading Factor | 2 |  | I3 | FLOAT | Wet Gas Overreading Factor | NV | No | R | - | - | - | -
|  | 312037 | Reserved foriNOC | 164

## iXC2-HR
CP | Tag Name | MODBUS HR | Description | No of Registers | Range | Comm Type | Data type | Remarks | Storage | On Demand | Access | UOM | Data Min | Data Max | Default
Gas Flow Measurement
| InpMdAGAP | 40001 | Input Mode for AGA Pressure | 1 | 0 to 2 | C3 | USHORT | Input Mode for AGA Pressure 0 - Local I/O Data 1 - Fixed Data 2 - Remote I/O Data | NV | No | R/W | - | 0 | 2 | 0
| InpMdAGATemp | 40002 | Input Mode for AGA Temperature | 1 | 0 to 2 | C3 | USHORT | Input Mode for AGA Temperature 0 - Local I/O Data 1 - Fixed Data 2 - Remote I/O Data | NV | No | R/W | - | 0 | 2 | 0
| InpMdAGADiffP | 40003 | Input Mode for AGA Differential Pressure | 1 | 0 to 2 | C3 | USHORT | Input Mode for AGA Differential Pressure 0 - Local I/O Data 1 - Fixed Data 2 - Remote I/O Data | NV | No | R/W | - | 0 | 2 | 0
| InpMdWCt | 40004 | Input Mode for Water Cut | 1 | 0 to 2 | C3 | USHORT | Input Mode for Water Cut 0 - Local I/O Data 1 - Fixed Data 2 - Remote I/O Data | NV | No | R/W | - | 0 | 2 | 0
| InpDensCalc | 40005 | Input Density Calculation Method | 1 | 1 to 6 | C3 | USHORT | Input Density Calculation Method 1 - AGA8 Gross 1 Method 2 - AGA8 Gross 2 Method 3 - AGA8 Detail Method 4 - Fixed Data (RHOTP and RHOS will be fixed values from HR) 5 - Local I/O Data (RHOTP will be from AI channel,RHOS will be fixed value from HR) 6 - Remote I/O Data (RHOTP will be from 3rd Party Device,RHOS will be fixed value from HR) | NV | No | R/W | - | 1 | 6 | 3
| InpMdAGARHOS | 40006 | Input Mode for AGA RHOS | 1 | 0 to 1 | C3 | USHORT | Input Mode for AGA RHOS 0 - AGA8 Output 1 - Fixed Data | NV | No | R/W | - | 0 | 1 | 0
| InpMdAGAZF | 40007 | Input Mode for AGA ZF | 1 | 0 to 1 | C3 | USHORT | Input Mode for AGA Compressibility Factor at Flowing condition (ZF) 0 - AGA8 Output 1 - Fixed Data | NV | No | R/W | - | 0 | 1 | 0
| InpMdAGAZB | 40008 | Input Mode for AGA ZB | 1 | 0 to 1 | C3 | USHORT | Input Mode for AGA Compressibility Factor at Base condition (ZB) 0 - AGA8 Output 1 - Fixed Data | NV | No | R/W | - | 0 | 1 | 0
| AGA7PulseSrc | 40009 | AGA7 Pulse Source | 1 | 0 to 2 | C3 | USHORT | AGA7 Pulse Source 0 - Pulse from DI 1 - Fixed Pulse from HR 2 - Remote I/O Data | NV | No | R/W | - | 0 | 2 | 0
| AGA79PulseTyp | 40010 | AGA7/9 Pulse type | 1 | 1 to 2 | C3 | USHORT | AGA7/9 Pulse type 1 - Pulse indicates Volume 2 - Pulse indicates Mass | NV | No | R/W | - | 1 | 2 | 1
| SeltPrcsPAIChNum | 40011 | Process Pressure Analog Input Channel No. | 1 | 2 to 8 | C3 | USHORT | Process Pressure Analog Input Channel No. AI1 and AI3 reserved for Load and Position Input respectively | NV | No | R/W | - | 2 | 8 | 2
| SeltPrcsTempAIChNum | 40012 | Process Temperature Analog Input Channel No | 1 | 2 to 9 | C3 | USHORT | Process Temperature Analog Input Channel No. AI1 and AI3 reserved for Load and Position Input respectively | NV | No | R/W | - | 2 | 9 | 8
| SeltPrcsDiffPAIChNum | 40013 | Process Differential Pressure Analog Input Channel No. | 1 | 2 to 8 | C3 | USHORT | Process Differential Pressure Analog Input Channel No. AI1 and AI3 reserved for Load and Position Input respectively | NV | No | R/W | - | 2 | 8 | 3
| SeltPrcsDensAIChNum | 40014 | Process Density Analog Input Channel No. (RHOTP) | 1 | 2 to 8 | C3 | USHORT | Process Density Analog Input Channel No. AI1 and AI3 reserved for Load and Position Input respectively | NV | No | R/W | - | 2 | 8 | 4
| SeltPrcsWCtAIChNum | 40015 | Process Water Cut Analog Input Channel No. | 1 | 2 to 8 | C3 | USHORT | Process Water Cut Analog Input Channel No. AI1 and AI3 reserved for Load and Position Input respectively | NV | No | R/W | - | 2 | 8 | 5
| AGA7InpPulseChNum | 40016 | AGA 7 Input Pulse channel Number | 1 | 9 | C3 | USHORT | AGA 7 Input Pulse channel Number( 9 - DI 9 Fixed) | NV | No | R/W | - |  | 9 | 9
| MID | 40017 | Meter Identifier | 6 |  | C3 | USHORT | Meter Identifier E.g. If Meter Identifier is ABC123, then user will enter HEX code in HR 0065 for 'A' 0066 for 'B' 0067 for 'C' 0049 for '1' 0050 for '2' 0051 for '3' Only Alpha-numeric characters are allowed. Writing HEX 0x00 will terminate the string and characters entered before the 0x00 will be considered as the Meter Identifier. | NV | No | R/W | - | - | - | -
| CmpyNm | 40023 | Company Name | 8 |  | C3 | USHORT | Company Name User will enter the characters in HEX code in HR same as Meter Identifier. Writing HEX 0x00 will terminate the string and characters entered before the 0x00 will be considered as the Company Name. | NV | No | R/W | - | - | - | -
| Loctn | 40031 | Location | 8 |  | C3 | USHORT | Location User will enter the characters in HEX code in HR same as Meter Identifier. Writing HEX 0x00 will terminate the string and characters entered before the 0x00 will be considered as the Location. | NV | No | R/W | - | - | - | -
| CntrctHr | 40039 | Contract Hour | 1 | 0 to 23 | C3 | USHORT | Contract Hour. 0 means Midnight, 1 means 1 AM, so hence and so forth | NV | No | R/W | - | 0 | 23 | 0
| FLRTmBase | 40040 | Flow Rate Time Base | 1 | 0 to 2 | C3 | USHORT | Flow Rate Time Base 0 - Flow Rate per Hour 1 - Flow Rate per Second 2 - Flow Rate per Day | NV | No | R/W | - | 0 | 2 | 0
| PEU | 40041 | Pressure Engineering Units | 1 | 1 to 3 | C3 | USHORT | Pressure Engineering Units 1 - Kilo pascal (kPa) 2 - Pounds per square inch (Psi) 3 - Bar | NV | No | R/W | - | 1 | 3 | 2
| DiffPEU | 40042 | Differential Pressure Engineering Units | 1 | 1 to 3 | C3 | USHORT | Differential Pressure Engineering Units 1 - Kilopascals (kPa) 2 - Inches of water (inWC) 3 - Millibars (mbar) | NV | No | R/W | - | 1 | 3 | 2
| TempEU | 40043 | Temperature Engineering Units | 1 | 1 to 2 | C3 | USHORT | Temperature Engineering Units 1 - Degrees celsius (°C) 2 - Degrees fahrenheit (°F) | NV | No | R/W | - | 1 | 2 | 2
| FLEU | 40044 | Flow Engineering Units | 1 | 1 to 8 | C3 | USHORT | Flow Engineering Units 1 - Million cubic meters (106m3, E6M3) 2 - Thousand cubic meters (103m3, E3M3) 3 - Hundred cubic meters (102m3) 4 - Cubic meters ( m3) 5 - Million cubic feet (MMcf) 6 - Thousand cubic feet (Mcf) 7 - Hundred cubic feet (Ccf) 8 - Cubic feet (cf) | NV | No | R/W | - | 1 | 8 | 6
| AGA3InpORFMatrlTyp | 40045 | AGA3 Input Orifice Material Type | 1 | 1 to 3 | C3 | USHORT | AGA3 Input Orifice Material (MATORF) 1 - Stainless Steel 2 - Monel 3 - Carbon | NV | No | R/W | - | 1 | 3 | 1
| AGA3InpPIPEMatrlTyp | 40046 | AGA3 Input Pipe Material Type | 1 | 1 to 3 | C3 | USHORT | AGA3 Input Pipe Material (MATPIPE) 1 - Stainless Steel 2 - Monel 3 - Carbon | NV | No | R/W | - | 1 | 3 | 3
| AGA3InpIFldTyp | 40047 | AGA3 Input Fluid Type | 1 | 1 to 2 | C3 | USHORT | AGA3 Input IFLUIDE 1 - Compressible Fluid 2 - Non-Compressible Fluid | NV | No | R/W | - | 1 | 2 | 1
| AGA3InpNPLOC | 40048 | AGA3 Input NPLOC | 1 | 1 to 2 | C3 | USHORT | AGA3 Input location of taps (NPLOC) 1 - Upstream 2 - Downstream | NV | No | R/W | - | 1 | 2 | 1
| HrlyRepSeltn | 40049 | Hourly Report Selection | 1 | 0 to 1440 | C3 | USHORT | Hourly Report Selection. Hourly Report for the selected hour is retrieved. 1 is the latest report and 1440 is the oldest. The value is reset to 0 once report data is updated in IR 6261 - 6284. | NV | No | R/W | - | 0 | 1440 | 0
| DailyRepSeltn | 40050 | Daily Report Selection | 1 | 0 to 60 | C3 | USHORT | Daily Report Selection. Daily Report for the selected hour is retrieved. 1 is the latest report and 60 is the oldest. The value is reset to 0 once report data is updated in IR 6301 - 6342. | NV | No | R/W | - | 0 | 60 | 0
|  | 40051 | Reserved | 2
| AGA3InpDOEU | 40053 | AGA3 DO Engeenering Unit | 1 | 1 or 2 | C3 | USHORT | AGA3 DO Engeenering Unit 1 - inches 2 - milli-meter | NV | No | R/W | - | 1 | 2 | 1
| AGA3InpDMEU | 40054 | AGA3 DM Engeenering Unit | 1 | 1 or 2 | C3 | USHORT | AGA3 DM Engeenering Unit 1 - inches 2 - milli-meter | NV | No | R/W | - | 1 | 2 | 1
| DensEU | 40055 | Density Engineering Unit | 1 | 1 or 2 | C3 | USHORT | Density Engineering Unit 1 - lbm/ft3 2 - kg/m3 | NV | No | R/W | - | 1 | 2 | 1
| UpdtEvt | 40056 | Update Events | 1 | 1 to 500 | C3 | USHORT | Update the Event in IR 6351 - 6361. It will reset to 0 once operation is completed | NV | No | R/W | - | 1 | 500 | 1
|  | 40057 | Reserved | 1 |  |  | USHORT
| ResetHstrclRprt | 40058 | Reset Historical Reports | 1 | 0 or 43690(Default: 0) | C3 | USHORT | Clear all the Daily and Hourly Reports. User has to write 43690 (HEX 0xAAAA) to clear the log files | NV | No | R/W |  | 0 | 43690 | 0
|  | 40059 | Reserved | 92 |  |  | USHORT
| BaseTemp | 40151 | Base Temperature (TB) | 2 | - | C3 | FLOAT | Base Temperature (TB) (Default Deg F) | NV | No | R/W | - |  |  | 60
| BaseP | 40153 | Base Pressure (PB) | 2 | - | C3 | FLOAT | Base Pressure (PB) (Default PSIA) | NV | No | R/W | - |  |  | 14.73
| AtmsphrcP | 40155 | Atmospheric Pressure | 2 | - | C3 | FLOAT | Atmospheric Pressure | NV | No | R/W | - |  |  | -
| PrcDPFix | 40157 | Process DP (DP) Fixed | 2 | 0 to 1000 | C3 | FLOAT | Process DP (DP) Fixed. (Default unit Inches H2O) | NV | No | R/W | - | 0 | 1000 | 0
| PrcPFix | 40159 | Process Pressure (PF) Fixed | 2 | 0 to 20000 | C3 | FLOAT | Process Pressure (PF) Fixed (Default PSIA) | NV | No | R/W | - | 0 | 20000 | 0
| PrcTempFix | 40161 | Process Temperature (TF) Fixed | 2 | -200 to 400 | C3 | FLOAT | Process Temperature (TF) Fixed (Default Deg F) | NV | No | R/W | - | -200 | 400 | 0
| PrcDensFix | 40163 | Process Density (RHOTP) Fixed | 2 | 0 to 200 | C3 | FLOAT | Process Density (RHOTP) Fixed (Default lbm/Ft3) | NV | No | R/W | - | 0 | 200 | 0
| WCtFix | 40165 | Water Cut Fixed | 2 | 0 to 100 | C3 | FLOAT | Water Cut Fixed (%) | NV | No | R/W | - | 0 | 100
| AGA7InpPulseCnt | 40167 | AGA 7 Input Pulse counts Fixed | 2 | 0 to 1000 | C3 | FLOAT | AGA 7 Input Pulse counts Fixed | NV | No | R/W | - | 0 | 1000 | 0
| RHOSFixed | 40169 | RHOS Fixed | 2 | - | C3 | FLOAT | Density at standard condition (RHOS Fixed) | NV | No | R/W | - |  |  | 0.046566
| ZBFixed | 40171 | ZB Fixed | 2 | - | C3 | FLOAT | Compressibility Factor (ZB Fixed) at base condition | NV | No | R/W | - |  |  | 0
| ZFFixed | 40173 | ZF Fixed | 2 | - | C3 | FLOAT | Compressibility Factor (ZF Fixed) at flowing condition | NV | No | R/W | - |  |  | 0
| FLCtOffLo | 40175 | Flow Cutoff Low | 2 |  | C3 | FLOAT | Flow Cutoff Low | NV | No | R/W | -
| MoleFrctn.C1 | 40177 | Mole Fraction Methane[X1] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Methane[X1] | NV | No | R/W | - | 0 | 1 | 0.81211
| MoleFrctn.GN2 | 40179 | Mole Fraction Nitrogen[X2] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Nitrogen[X2] | NV | No | R/W | - | 0 | 1 | 0.05702
| MoleFrctn.CO2 | 40181 | Mole Fraction Carbon Dioxide[X3] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Carbon Dioxide[X3] | NV | No | R/W | - | 0 | 1 | 0.07585
| MoleFrctn.C2H6 | 40183 | Mole Fraction Ethane[X4] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Ethane[X4] | NV | No | R/W | - | 0 | 1 | 0.04303
| MoleFrctn.C3 | 40185 | Mole Fraction Propane[X5] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Propane[X5] | NV | No | R/W | - | 0 | 1 | 0.00895
| MoleFrctn.W | 40187 | Mole Fraction Water Mole[X6] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Water Mole[X6] | NV | No | R/W | - | 0 | 1 | 0
| MoleFrctn.H2S | 40189 | Mole Fraction Hydrogen Sulfide[X7] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Hydrogen Sulfide[X7] | NV | No | R/W | - | 0 | 1 | 0
| MoleFrctn.H2 | 40191 | Mole Fraction Hydrogen[X8] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Hydrogen[X8] | NV | No | R/W | - | 0 | 1 | 0
| MoleFrctn.CO | 40193 | Mole Fraction Carbon Monoxide[X9] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Carbon Monoxide[X9] | NV | No | R/W | - | 0 | 1 | 0
| MoleFrctn.O2 | 40195 | Mole Fraction Oxygen[X10] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Oxygen[X10] | NV | No | R/W | - | 0 | 1 | 0
| MoleFrctn.IC4H10 | 40197 | Mole Fraction I-Butane[X11] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction I-Butane[X11] | NV | No | R/W | - | 0 | 1 | 0.00151
| MoleFrctn.NC4H10 | 40199 | Mole Fraction N-Butane[X12] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction N-Butane[X12] | NV | No | R/W | - | 0 | 1 | 0.00151
| MoleFrctn.IC5H12 | 40201 | Mole Fraction I-Pentane[X13] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction I-Pentane[X13] | NV | No | R/W | - | 0 | 1 | 0
| MoleFrctn.NC5H12 | 40203 | Mole Fraction N-Pentane[X14] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction N-Pentane[X14] | NV | No | R/W | - | 0 | 1 | 0
| MoleFrctn.C6 | 40205 | Mole Fraction Hexane[X15] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Hexane[X15] | NV | No | R/W | - | 0 | 1 | 0
| MoleFrctn.C7H16 | 40207 | Mole Fraction Heptane[X16] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Heptane[X16] | NV | No | R/W | - | 0 | 1 | 0
| MoleFrctn.C8H18 | 40209 | Mole Fraction Octane[X17] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Octane[X17] | NV | No | R/W | - | 0 | 1 | 0
| MoleFrctn.C9H20 | 40211 | Mole Fraction Nonane[X18] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Nonane[X18] | NV | No | R/W | - | 0 | 1 | 0
| MoleFrctn.C10H22 | 40213 | Mole Fraction Decane[X19] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Decane[X19] | NV | No | R/W | - | 0 | 1 | 0
| MoleFrctn.He | 40215 | Mole Fraction Helium[X20] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Helium[X20] | NV | No | R/W | - | 0 | 1 | 0
| MoleFrctn.Ar | 40217 | Mole Fraction Argon[X21] | 2 | 0 to 1 | C3 | FLOAT | Mole Fraction Argon[X21] | NV | No | R/W | - | 0 | 1 | 0
| AGA8InpHV | 40219 | AGA8 Input HV | 2 | 477 to 1150 | C3 | FLOAT | AGA8 Input Heating Value (HV) | NV | No | R/W | - |  |  | 933.12
| AGA8InpGRGR | 40221 | AGA8 Input GRGR | 2 | 0.554 to 0.87 | C3 | FLOAT | Relative density of gas mixture (GRGR) | NV | No | R/W | - |  |  | 0.686
| AGA3InpDO | 40223 | AGA3 Input DO | 2 | 0.45 to 100 | C3 | FLOAT | Orifice plate bore diameter calculated at flowing temperature (DO) (Default in Inches) | NV | No | R/W | - | 0.45 | 100 | 0.5
| AGA3InpTORF | 40225 | AGA3 Input TORF | 2 | - | C3 | FLOAT | Orifice Diameter Measurement Temperature (TORF) | NV | No | R/W | - | - | - | 68
| AGA3InpDM | 40227 | AGA3 Input DM | 2 | 0 to 100 | C3 | FLOAT | Meter tube internal diameter calculated at flowing temperature (DM) (Default in Inches) | NV | No | R/W | - | 0 | 100 | 2.9004
| AGA3InpTPIPE | 40229 | AGA3 Input TPIPE | 2 | - | C3 | FLOAT | PIPE diameter measurement temperature (TPIPE) | NV | No | R/W | - |  |  | 68
| AGA3InpVISC | 40231 | AGA3 Input VISC | 2 | 0.005 to 0.5 | C3 | FLOAT | AGA3 Input Viscosity (VISC) (In CENTIPOISES) | NV | No | R/W | - | 0.005 | 0.5 | 0.010268
| AGA3InpKFAC | 40233 | AGA3 Input KFAC | 2 | 1 to 2 | C3 | FLOAT | Isentropic exponent (KFAC) | NV | No | R/W | - | 1 | 2 | 1.3
| AGA3InpFACTR | 40235 | AGA3 Input FACTR | 2 | - | C3 | FLOAT | User factor multiplied together (both pipe & flange) (FACTR) | NV | No | R/W | - | - | - | 1
| AGA3InpZAIRS | 40237 | AGA3 Input ZAIRS | 2 | - | C3 | FLOAT | Compressibility factor of air at standard condition (ZAIRS) | NV | No | R/W | - | - | - | 0.99958
| AGA3InpZAIRB | 40239 | AGA3 Input ZAIRB | 2 | - | C3 | FLOAT | Compressibility factor of air at base condition (ZAIRB) | NV | No | R/W | - | - | - | 0.99959
| AGA7InpKF | 40241 | AGA7 Input KF | 2 | - | C3 | FLOAT | k-factor to provide specific no. of pulses per unit volume | NV | No | R/W | - | - | - | 0
| AGA7InpMF | 40243 | AGA7 Input MF | 2 | 0 to 1.5 | C3 | FLOAT | Meter Factor adjustment (MF AGA7 Input) | NV | No | R/W | - | 0 | 1.5 | 0
| AGA7InpPulseCtOff | 40245 | AGA7 Input Pulse Cut-Off | 2 | - | C3 | FLOAT | AGA 7 Input Pulse Cut-Off | NV | No | R/W | - | - | - | 0
| AGA7InpLF | 40247 | AGA7 Input LF (12 Linear factors) | 24 | - | C3 | FLOAT | AGA 7 Input Linear Factor ( 12 Linear factors ) | NV | No | R/W | - | - | - | 0
| AGA7InpLFTH | 40271 | AGA7 Input LFTH (12 Linear factor thresholds) | 24 | - | C3 | FLOAT | AGA 7 Input Linear Factor threshold ( 12 Linear factor thresholds) | NV | No | R/W | - | - | - | 0
| AlmLoSPLocRemPF | 40295 | Alarm Low Set Point for Local/Remote PF | 2 | - | C3 | FLOAT | Alarm Low Set Point for Local/Remote PF | NV | No | R/W | - | - | -
| AlmHiSPLocRemPF | 40297 | Alarm High Set Point for Local/Remote PF | 2 | - | C3 | FLOAT | Alarm High Set Point for Local/Remote PF | NV | No | R/W | - | - | -
| AlmLoSPLocRemTF | 40299 | Alarm Low Set Point for Local/Remote TF | 2 | - | C3 | FLOAT | Alarm Low Set Point for Local/Remote TF | NV | No | R/W | - | - | -
| AlmHiSPLocRemTF | 40301 | Alarm High Set Point for Local/Remote TF | 2 | - | C3 | FLOAT | Alarm High Set Point for Local/Remote TF | NV | No | R/W | - | - | -
| AlmLoSPLocRemDiffP | 40303 | Alarm Low Set Point for Local/Remote Diff. Pressure | 2 | - | C3 | FLOAT | Alarm Low Set Point for Local/Remote Diff. Pressure | NV | No | R/W | - | - | -
| AlmHiSPLocRemDiffP | 40305 | Alarm High Set Point for Local/Remote Diff. Pressure | 2 | - | C3 | FLOAT | Alarm High Set Point for Local/Remote Diff. Pressure | NV | No | R/W | - | - | -
| AlmLoSPLocRemDens | 40307 | Alarm Low Set Point for Local/Remote Density | 2 | - | C3 | FLOAT | Alarm Low Set Point for Local/Remote Density | NV | No | R/W | - | - | -
| AlmHiSPLocRemDens | 40309 | Alarm High Set Point for Local/Remote Density | 2 | - | C3 | FLOAT | Alarm High Set Point for Local/Remote Density | NV | No | R/W | - | - | -
| AlmLoSPLocRemWCt | 40311 | Alarm Low Set Point for Local/Remote Water Cut | 2 | - | C3 | FLOAT | Alarm Low Set Point for Local/Remote Water Cut | NV | No | R/W | - | - | -
| AlmHiSPLocRemWCt | 40313 | Alarm High Set Point for Local/Remote Water Cut | 2 | - | C3 | FLOAT | Alarm High Set Point for Local/Remote Water Cut | NV | No | R/W | - | - | -
| FLRHi | 40315 | Flow rate High | 2 | - | C3 | FLOAT | Flow rate High (Cubic Feets) | NV | No | R/W | - | - | -
| FLRLo | 40317 | Flow rate Low | 2 | - | C3 | FLOAT | Flow rate Low | NV | No | R/W | - | - | -
| AlmDBPrcsP | 40319 | Alarm deadband for PF | 2 | - | C3 | FLOAT | Alarm deadband for flowing pressure (PF) | NV | No | R/W | - | - | -
| AlmDBPrcsTemp | 40321 | Alarm deadband for TF | 2 | - | C3 | FLOAT | Alarm deadband for flowing temperature (TF) | NV | No | R/W | - | - | -
| AlmDBPrcsDiffP | 40323 | Alarm deadband for Diff. Pressure | 2 | - | C3 | FLOAT | Alarm deadband for Differential Pressure (DP) | NV | No | R/W | - | - | -
| AlmDBPrcsDens | 40325 | Alarm deadband for Density | 2 | - | C3 | FLOAT | Alarm deadband for Density | NV | No | R/W | - | - | -
| AlmDBPrcsWCt | 40327 | Alarm deadband for Water Cut | 2 | - | C3 | FLOAT | Alarm deadband for Water Cut | NV | No | R/W | - | - | -
| AlmDBFLR | 40329 | Alarm deadband for Flow Rate | 2 | - | C3 | FLOAT | Alarm deadband for Flow Rate | NV | No | R/W | - | - | -
|  | 40331 | Reserved for Flow Computer | 1670 |  |  | USHORT
|  | 42001 | Reserved for Applications | 6000
RTU Kernel
| FileDelOptns | 48001 | File Delete Options | 1 | 0 to 2 | C3 | USHORT | 0 - No File Delete 1 - Delete all MB Files and Exit 2 - Delete all MB Files and Reboot | NV | No | R/W | - | 0 | 2 | 0
| NewBrdTm | 48002 | New RTU Time (UTC) | 2 | - | C3 | LONG | Set New Board Time | NV | No | R/W | UTC Seconds | - | - | -
| TmZone | 48004 | Time Zone UTC – Offset in minutes | 1 | -720 to 840 | C3 | SHORT | Set New Time Zone | NV | No | R/W | Min | -720 | 840 | 240
| TmSync.Mo | 48005 | Time Synchronization – Month | 1 | - | C3 | USHORT | These are the time synchronization registers. When user writes to these registers and sets CS 8100 to 1, the new board time will be set. The time synchronization registers HR 8005 - 8010 and CS 8100 will be reset to 0. | NV | No | R/W | MM | - | - | -
| TmSync.Da | 48006 | Time Synchronization – Day | 1 | - | C3 | USHORT |  | NV | No | R/W | DD | - | - | -
| TmSync.Yr | 48007 | Time Synchronization – Year | 1 | - | C3 | USHORT |  | NV | No | R/W | YY | - | - | -
| TmSync.Hr | 48008 | Time Synchronization – Hour | 1 | - | C3 | USHORT |  | NV | No | R/W | Hr | - | - | -
| TmSync.Mins | 48009 | Time Synchronization – Minutes | 1 | - | C3 | USHORT |  | NV | No | R/W | Min | - | - | -
| TmSync.Secs | 48010 | Time Synchronization – Seconds | 1 | - | C3 | USHORT |  | NV | No | R/W | Sec | - | - | -
| StsMsgLgr | 48011 | Status of Message Logger | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 1
| StsAlmMngr | 48012 | Status of Alarm Manager | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
| StsDtLgr | 48013 | Status of Data Logger | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
| StsIODtAcqtn | 48014 | Status of IO_DataAcquisition | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 1
| StsMBRTUMstr | 48015 | Status of MB RTU Master | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
| StsMBRTUSlv | 48016 | Status of MB RTU Slave | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
| StsMBTCPMstr | 48017 | Status of MB TCP Master | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
| StsMBTCPSlv | 48018 | Status of MB TCP Slave | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 1
|  | 48019 | Reserved for Debug | 4
| StsWebSvr | 48023 | Status of Web Server | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 1
| StsWetGDtctn | 48024 | Status of Wet Gas detection | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
|  | 48025 | Reserved for Debug | 1
| StsISaGRAF | 48026 | Status of IsaGRAF | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
|  | 48027 | Reserved for Debug | 1 |  |  | USHORT
| StsAGA | 48028 | Status of AGA | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
|  | 48029 | Reserved for Debug | 2 |  |  | USHORT
| StsDNP3Slv | 48031 | Status of DNP3 Slave | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
| StsDNP3Mstr | 48032 | Status of DNP3 Master | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
|  | 48033 | Reserved for Debug | 2 |  |  | USHORT
| StsWMP | 48035 | Status of WMP | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 1
|  | 48036 | Reserved for Debug | 1 |  |  | USHORT
| StsEnrnMBSlv | 48037 | Status of Enron MB Slave | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
|  | 48038 | Reserved for Debug | 3 |  |  | USHORT
| StsEthIP | 48041 | Status of Ethernet IP | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
|  | 48042 | Reserved for Debug | 3 |  |  | USHORT
| StsMBDtCpy | 48045 | Status of MB Data Copier | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
| StsBOM | 48046 | Status of Black Oil Model | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
| StsMQTTCliA | 48047 | Status of MQTT Client A | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
| StsMQTTCliB | 48048 | Status of MQTT Client B | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
| StsLcnsMngr | 48049 | Status of License Manager | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
| StsPrvsng | 48050 | Status of Provisioning | 1 | 0 to 2 | C3 | USHORT | 0 = Stop the module 1 = Start the module 2 = Stop and start module and set HR = 1; | NV | No | R/W | - | 0 | 2 | 0
|  | 48051 | Reserved | 50
| SetManTmSynciXC2 | 48101 | Set Manual Time sync of iXC2 | 1 | 0 or 1 | C3 | USHORT | Manual Time Synhronization Register. When user sets 1 to this register, board time is updated with the values in HR 8102 - 8104. | NV | No | R/W | - | 0 | 1 | 0
| PrdfdTmSyncHr | 48102 | Predefined Time Synchronization – Hour | 1 | 0 to 23 | C3 | USHORT | Predefined Synchronization Time. When user sets 1 in HR 8101, then board time(Hour, Minute, Second) will be updated with this time. It will maintain the Day, Month and Year. | NV | No | R/W | Hr | 0 | 23 | 0
| PrdfdTmSyncMins | 48103 | Predefined Time Synchronization – Minutes | 1 | 0 to 59 | C3 | USHORT |  | NV | No | R/W | Min | 0 | 59 | 0
| PrdfdTmSyncSecs | 48104 | Predefined Time Synchronization – Seconds | 1 | 0 to 59 | C3 | USHORT |  | NV | No | R/W | Sec | 0 | 59 | 0
| TmZoneIndex | 48105 | Time Zone Index | 1 | 1 to 135 | C3 | USHORT | Set new time zone based on Index. For Index value of time zones please refer to TimeZone sheet | NV | No | R/W |  | 1 | 135
|  | 48106 | Reserved | 85
ISaGRAF
| EnblDsblRes1 | 48191 | Enable/Disable Resource 1 | 1 | 0 to 3 | C3 | USHORT | 0 = No Action - ISaGRAF resets this to 0 once action is taken 1 = Stop Resource 1 2 = Start Resource 1 3 = Restart Resource 1 CS 8251 must be set after this to trigger the process. | NV | No | R/W |  | 0 | 3 | 0
| EnblDsblRes2 | 48192 | Enable/Disable Resource 2 | 1 | 0 to 3 | C3 | USHORT | 0 = No Action - ISaGRAF resets this to 0 once action is taken 1 = Stop Resource 2 2 = Start Resource 2 3 = Restart Resource 2 CS 8252 must be set after this to trigger the process. | NV | No | R/W |  | 0 | 3 | 0
| EnblDsblRes3 | 48193 | Enable/Disable Resource 3 | 1 | 0 to 3 | C3 | USHORT | 0 = No Action - ISaGRAF resets this to 0 once action is taken 1 = Stop Resource 3 2 = Start Resource 3 3 = Restart Resource 3 CS 8253 must be set after this to trigger the process. | NV | No | R/W |  | 0 | 3 | 0
| EnblDsblRes4 | 48194 | Enable/Disablet Resource 4 | 1 | 0 to 3 | C3 | USHORT | 0 = No Action - ISaGRAF resets this to 0 once action is taken 1 = Stop Resource 4 2 = Start Resource 4 3 = Restart Resource 4 CS 8254 must be set after this to trigger the process. | NV | No | R/W |  | 0 | 3 | 0
|  | 48195 | Reserved | 6
Input Output
| AOCh1 | 48201 | Analog Output channel1 (AO1) | 1 | 0 to 4095 | O3 | USHORT | Analog Output Count (DAC) for AO1 | NV | No | R/W | - | 0 | 4095 | 819
| AOCh2 | 48202 | Analog Output channel2 (AO2) | 1 | 0 to 4095 | O3 | USHORT | Analog Output Count (DAC) for AO2 | NV | No | R/W | - | 0 | 4095 | 819
|  | 48203 | Reserved | 1 |  |  | USHORT
|  | 48204 | Reserved | 3
|  | 48207 | Reserved for Debug | 1 |  |  | USHORT
|  | 48208 | Reserved for Debug | 1 |  |  | USHORT
|  | 48209 | Reserved | 5
|  | 48214 | Reserved for Debug | 1 |  |  | USHORT
|  | 48215 | Reserved | 3
|  | 48218 | Reserved for internal use only | 2 |  |  | ULONG
|  | 48220 | Reserved | 3
| MinRawCntAI1 | 48223 | Minimum Raw count for AI1 | 2 | 0 to 16777215 | C3 | ULONG | Minimum Raw Count for AI1 | NV | No | R/W | - | 0 | 16777215 | 1310720
| MaxRawCntAI1 | 48225 | Maximum Raw count for AI1 | 2 | 0 to 16777215 | C3 | ULONG | Maximum Raw Count for AI1 | NV | No | R/W | - | 0 | 16777215 | 6553600
|  | 48227 | Reserved | 4
| EULoLimAI1 | 48231 | Engineering Unit Low Limit for AI1 | 2 | - | C3 | FLOAT | EU Low limit for AI 1 | NV | No | R/W | - | - | - | 0
| EUHiLimAI1 | 48233 | Engineering Unit High Limit for AI1 | 2 | - | C3 | FLOAT | EU High limit for AI 1 | NV | No | R/W | - | - | - | 1500
| MinRawCntAI2 MaxRawCntAI2 EULoLimAI2 EUHiLimAI2 | 48235 | Minimum and Maximum raw count, Engineering Unit Low and High for AI2 channel, similar to 8223 to 8234 registers | 12 | - | C3 | - | Same as above for AI 2 | NV | No | R/W | - | - | - | -
| MinRawCntAI3 MaxRawCntAI3 EULoLimAI3 EUHiLimAI3 | 48247 | Minimum and Maximum raw count, Engineering Unit Low and High for AI3 channel, similar to 8223 to 8234 registers | 12 | - | C3 | - | Same as above for AI 3 | NV | No | R/W | - | - | - | -
| MinRawCntAI4 MaxRawCntAI4 EULoLimAI4 EUHiLimAI4 | 48259 | Minimum and Maximum raw count, Engineering Unit Low and High for AI4 channel, similar to 8223 to 8234 registers | 12 | - | C3 | - | Same as above for AI 4 | NV | No | R/W | - | - | - | -
| MinRawCntAI5 MaxRawCntAI5 EULoLimAI5 EUHiLimAI5 | 48271 | Minimum and Maximum raw count, Engineering Unit Low and High for AI5 channel, similar to 8223 to 8234 registers | 12 | - | C3 | - | Same as above for AI 5 | NV | No | R/W | - | - | - | -
| MinRawCntAI6 MaxRawCntAI6 EULoLimAI6 EUHiLimAI6 | 48283 | Minimum and Maximum raw count, Engineering Unit Low and High for AI6 channel, similar to 8223 to 8234 registers | 12 | - | C3 | - | Same as above for AI 6 | NV | No | R/W | - | - | - | -
| MinRawCntAI7 MaxRawCntAI7 EULoLimAI7 EUHiLimAI7 | 48295 | Minimum and Maximum raw count, Engineering Unit Low and High for AI7 channel, similar to 8223 to 8234 registers | 12 | - | C3 | - | Same as above for AI 7 | NV | No | R/W | - | - | - | -
| MinRawCntAI8 MaxRawCntAI8 EULoLimAI8 EUHiLimAI8 | 48307 | Minimum and Maximum raw count, Engineering Unit Low and High for AI8 channel, similar to 8223 to 8234 registers | 12 | - | C3 | - | Same as above for AI 8 | NV | No | R/W | - | - | - | -
|  | 48319 | Reserved | 24
| DO1PulseDrtn | 48343 | Digital Output 1 Pulse Duration | 1 | 0 to 65535 | C3 | USHORT | Digital Output 1 Pulse Duration Interval. This is applicable when Digital Output 1 Type HR 8351 is set to 2 i.e. Pulse Output Mode. | NV | No | R/W | - | 0 | 65535 | 0
| DO2PulseDrtn, DO8PulseDrtn | 48344 | Digital Output 2 to 8 Pulse Duration | 7 | 0 to 65535 | C3 | USHORT | Digital Output 2 to 8 Pulse Duration Interval. It is applicable only when HR 8352 - 8358 are set to 2 for DO2 - DO8 respectively. | NV | No | R/W | - | 0 | 65535 | 0
| DO1Typ, DO8Typ | 48351 | Digital Output Type for DO1 to DO8 | 8 | 1 or 2 | C3 | USHORT | Digital Output Type 1 - Digital Output Mode 2 - Pulse Output Mode If the corresponding DO is in Pulse Output Mode then only respective Pulse Duration in HR 8343 - 8350 is applicable. | NV | No | R/W | - | 1 | 2 | 1
|  | 48359 | Reserved | 24
| AI1Typ, AI8Typ | 48383 | Analog Input Type for AI1 to AI8 | 8 | 1 or 2 | C3 | USHORT | If AI type changed then raw min and max count should be changed. 1 - Current 2 - Voltage | NV | No | R/W | - | 1 | 2 | 1
| AI9Typ | 48391 | Analog Input Type for AI 9 | 1 | - | C3 | USHORT | AI Channel 9 Type 4 - Temperature | NV | No | R/W | - | - | - | 4
| AI10Typ | 48392 | Analog Input Type for AI 10 | 1 | 3 or 5 | C3 | USHORT | AI Channel 10 Type 3 - Battery 5 - Humidity | NV | No | R/W | - | 3 | 5 | 3
| DI1Typ, DI8Typ | 48393 | Digital Input Type for DI1 to DI8 | 8 | 0 to 2 | C3 | USHORT | Digital Input Type for DI 1 to DI 8 0 - Digital 1 - Pulse Counter 2 - Pulse Accumulation | NV | No | R/W | - | 0 | 2 | 0
| DI9Typ | 48401 | Digital Input Type for DI9 | 1 | 0 to 3 | C3 | USHORT | Digital Input Type for DI 9 0 - Digital 1 - Pulse Counter 2 - Pulse Accumulation 3 - Pulse Per Minute | NV | No | R/W | - | 0 | 3 | 2
| AO1Typ, AO2Typ | 48402 | Analog Output Type for AO1 to AO2 | 2 | 1 or 2 | C3 | USHORT | Analog Output Type 1 - Current 2 - Voltage | NV | No | R/W | - | 1 | 2 | 1
| CoEffAO1CTypAO | 48404 | Co-efficient for AO1, for AO as current type | 2 | - | C3 | FLOAT | - | NV | No | R/W | - | - | - | -
| CoEffAO2CTypAO | 48406 | Co-efficient for AO2, for AO as current type | 2 | - | C3 | FLOAT | - | NV | No | R/W | - | - | - | -
| ContAO1CTypAO | 48408 | Constant for AO1, for AO as current type | 2 | - | C3 | FLOAT | - | NV | No | R/W | - | - | - | -
| ContAO2CTypAO | 48410 | Constant for AO2, for AO as current type | 2 | - | C3 | FLOAT | - | NV | No | R/W | - | - | - | -
|  | 48412 | Reserved | 14 |  |  | FLOAT
| AIChCalibTyp | 48426 | Analog Input Channel Calibration Type | 1 | 0 to 2 | C3 | USHORT | AI Calibration Type 0- Raw 1- Current 2- Voltage | NV | No | R/W | - | 0 | 2 | 0
| CalibLoAI1 | 48427 | Calibration Low for AI1 | 2 | 0 to 16777215 | C3 | FLOAT | Calibration Range | NV | No | R/W | - | 0 | 16777215 | 1310720
| CalibHiAI1 | 48429 | Calibration High for AI1 | 2 | 0 to 16777215 | C3 | FLOAT |  | NV | No | R/W | - | 0 | 16777215 | 6553600
| CalibLoAI2 CalibHiAI2 | 48431 | Calibration Low and High for AI2, similar to 8427 to 8430 (calibration range) | 4 | - | C3 | FLOAT | Same as above for AI 2 | NV | No | R/W | - | - | - | -
| CalibLoAI3 CalibHiAI3 | 48435 | Calibration Low and High for AI3, similar to 8427 to 8430 (calibration range) | 4 | - | C3 | FLOAT | Same as above for AI 3 | NV | No | R/W | - | - | - | -
| CalibLoAI4 CalibHiAI4 | 48439 | Calibration Low and High for AI4, similar to 8427 to 8430 (calibration range) | 4 | - | C3 | FLOAT | Same as above for AI 4 | NV | No | R/W | - | - | - | -
| CalibLoAI5 CalibHiAI5 | 48443 | Calibration Low and High for AI5, similar to 8427 to 8430 (calibration range) | 4 | - | C3 | FLOAT | Same as above for AI 5 | NV | No | R/W | - | - | - | -
| CalibLoAI6 CalibHiAI6 | 48447 | Calibration Low and High for AI6, similar to 8427 to 8430 (calibration range) | 4 | - | C3 | FLOAT | Same as above for AI 6 | NV | No | R/W | - | - | - | -
| CalibLoAI7 CalibHiAI7 | 48451 | Calibration Low and High for AI7, similar to 8427 to 8430 (calibration range) | 4 | - | C3 | FLOAT | Same as above for AI 7 | NV | No | R/W | - | - | - | -
| CalibLoAI8 CalibHiAI8 | 48455 | Calibration Low and High for AI8, similar to 8427 to 8430 (calibration range) | 4 | - | C3 | FLOAT | Same as above for AI 8 | NV | No | R/W | - | - | - | -
|  | 48459 | Reserved | 4
|  | 48463 | Reserved | 4
|  | 48467 | Reserved for Debug | 2 |  |  | ULONG
|  | 48469 | Reserved for Debug | 1 |  |  | USHORT
|  | 48470 | Reserved for Debug | 1 |  |  | USHORT
|  | 48471 | Reserved for Debug | 1 |  |  | USHORT
| AI1RngSeltn, AI8RngSeltn | 48472 | AI input Range selection, for AI1 to AI10 [Applicable in Voltage mode only] | 8 | 0 to 9 | C3 | USHORT | AI Range Selection. Range 8 and 9 are applicable only if the channel is in Differential Mode. 9 - 0 to 10.24 v 8 - -5.12v to 5.12 v 7 - 0 to 5.12 v 6 - 0 to 2.56 v 5 - 0 to 1.28 v 4 - 0 to 640 mv 3 - 0 to 320 mv 2 - 0 to 160 mv 1 - 0 to 80 mv 0 - 0 to 40 mv | NV | No | R/W | - | 0 | 9 | 7
|  | 48480 | Reserved for Debug | 2
| DfltAO1PwrUp | 48482 | Default AO1 value at Power ON depending on the status bit CS:8111 | 1 | 0 to 4095 | C3 | USHORT | This is the Default AO1 value. If CS 8111 is set to 0, this value will be updated in HR 8201 at Power ON. | NV | No | R/W | - | 0 | 4095 | 819
| DfltAO2PwrUp | 48483 | Default AO2 value at Power ON depending on the status bit CS:8111 | 1 | 0 to 4095 | C3 | USHORT | This is the Default AO2 value. If CS 8112 is set to 0, this value will be updated in HR 8202 at Power ON. | NV | No | R/W | - | 0 | 4095 | 819
|  | 48484 | Reserved for Debug | 41 |  |  | USHORT
| SetEUValAO1 | 48525 | Set EU Value for AO1 | 2 | ln Voltage Mode : 0 to 5 In Current Mode : 4 to 20 | C3 | FLOAT | EU Values for AO1. Depending upon the AO mode(Current or Voltage) in HR 8402 the range will very. | NV | No | R/W | - | ln Voltage Mode : 0 In Current Mode : 4 | ln Voltage Mode :5 In Current Mode : 20 | 0/4
| SetEUValAO2 | 48527 | Set EU Value for AO2 | 2 | ln Voltage Mode : 0 to 5 In Current Mode : 4 to 20 | C3 | FLOAT | EU Values for AO2. Depending upon the AO mode(Current or Voltage) in HR 8403 the range will very. | NV | No | R/W | - | ln Voltage Mode : 0 In Current Mode : 4 | ln Voltage Mode :5 In Current Mode : 20 | 0/4
|  | 48529 | Reserved for Debug | 1 |  |  | USHORT
|  | 48530 | Reserved for internal use only | 1 |  |  | HEX
| DI1StsIntrvl, DI9StsIntrvl | 48531 | DI Status Debouncing Interval in Millisecond for DI1 to DI9 | 9 | 0 to 100 | C3 | USHORT | DI Debouncing Interval for DI1 to DI9. This is the interval the input must be maintained to change state. | NV | No | R/W | mSec | 0 | 100 | 15
|  | 48540 | Reserved | 1 |  |  | USHORT
|  | 48541 | Reserved | 1 |  |  | USHORT
| PrcntAO1EU | 48542 | Percent value of AO with respect to EU for AO1 | 2 | 0 to 100 | C3 | FLOAT |  | NV | No | R/W | % | 0 | 100 | 0
| PrcntAO2EU | 48544 | Percent value of AO with respect to EU for AO2 | 2 | 0 to 100 | C3 | FLOAT |  | NV | No | R/W | % | 0 | 100 | 0
| DfltEUValAO1 | 48546 | Default Set EU Value for AO1 depending on the status bit CS:8111 | 2 | ln Voltage Mode : 0 to 5 In Current Mode : 4 to 20 | C3 | FLOAT | This is the Default EU value for AO1. If CS 8111 is set to 0, this value will be updated in HR 8525 - 8526 at Power ON. | NV | No | R/W | - | - | - | -
| DfltEUValAO2 | 48548 | Default Set EU Value for AO2 depending on the status bit CS:8112 | 2 | ln Voltage Mode : 0 to 5 In Current Mode : 4 to 20 | C3 | FLOAT | This is the Default EU value for AO2. If CS 8112 is set to 0, this value will be updated in HR 8527 - 8528 at Power ON. | NV | No | R/W | - | - | - | -
| DfltPrcntValAO1 | 48550 | Default Percent value of AO with respect to EU for AO1 depending on the status bit CS:8111 | 2 | 0 to 100 | C3 | FLOAT | This is the Default Percentage value for AO1. If CS 8111 is set to 0, this value will be updated in HR 8542 - 8543 at Power ON. | NV | No | R/W | % | 0 | 100 | 0
| DfltPrcntValAO2 | 48552 | Default Percent value of AO with respect to EU for AO2 depending on the status bit CS:8112 | 2 | 0 to 100 | C3 | FLOAT | This is the Default Percentage value for AO2. If CS 8112 is set to 0, this value will be updated in HR 8544 - 8545 at Power ON. | NV | No | R/W | % | 0 | 100 | 0
| EnblAIScl1, EnblAIScl8 | 48554 | Enable AI Input scale up 22 mA for AI1 to AI8 | 8 | 0 or 1 | C3 | USHORT | Writing 1 to this register enables scale upto 22 mA of particular channel. | NV | No | R/W | - | 0 | 1 | 0
|  | 48562 | Reserved | 129
Data Logger
| ClearDtLgr | 48691 | Clear Data Logger Files | 1 | 0 or 21845 | C3 | USHORT | Clear all the Data Logger Single/Common files present in the Log/Datalog folder. User has to write 21845 (HEX 0x5555) to clear the log files. Same has to be entered from Web Server. | NV | No | R/W | - | 0 | 21845 | 0
| USBManTrgr | 48692 | USB Manual Trigger | 1 | 0 or 41120 | C3 | USHORT | Manual Trigger Register. User has to write 41120 (HEX 0xA0A0) to copy all the files in Log/Datalog folder to the mounted USB | NV | No | R/W | - | 0 | 41120 | 0
| DtPtNum | 48693 | Data Point Number | 1 | 0 to 100,1000 | C3 | USHORT | This is the Data Point Number or the Common Data for which user wants read/modify/configure the Parameter. 1 to 100 - Data Point Number 1000 - Common Data It will reset to 0 once the process is completed. | NV | No | R/W | - | 0 | 1000 | 0
| PrmtrNum | 48694 | Parameter Number | 1 | 0 to 4 | C3 | USHORT | This is the Parameter Number for which user wants to read/modify/configure the value. The Data Point/Common Data will be as mentioned in HR 8693. It will reset to 0 once the process is completed. 1 - Log Interval 2 - Common Log Interval 3 - File Create Option 4 - Disk Full Option | NV | No | R/W | - | 0 | 4 | 0
| PrmtrVal | 48695 | Parameter Value | 2 |  | C3 | FLOAT | This is the Parameter value for the Parameter for which user wants to modify/configure the value. The Data Point/Common Data will be as mentioned in HR 8693 and Parameter Number in HR 8694. It will reset to 0 once the process is completed. | NV | No | R/W | - |  |  | 0
|  | 48697 | Reserved | 4
|  | MB TCP Slave | [10 empty] | - | - | -
| MBTCPSlvReset | 48701 | MB_TCP_Slave statistic reset. Writing 1 - 247 will reset statistic data for that ID. Writing 1000 will reset the data for all the IDs. | 1 | 0 to 247, 1000 | C3 | SHORT | MB TCP Slave statistic reset. 1 to 247 - Reset the statistics of particular ID 100 - Reset statistics of all IDs It resets to 0 once process is completed. | NV | No | R/W | - | 0 | 1000 | 0
|  | 48702 | Reserved | 49
MB Master
| MBRTUMstrReset | 48751 | MB_RTU_Master statistic reset. Writing 1 - 247 will reset statistic data for that ID. Writing 1000 will reset the data for all the IDs. | 1 | 0 to 247, 1000 | C3 | SHORT | MB RTU Master statistic reset. 1 to 247 - Reset the statistics of particular ID 100 - Reset statistics of all IDs It resets to 0 once process is completed. | NV | No | R/W | - | 0 | 1000 | 0
| MBTCPMstrReset | 48752 | MB_TCP_Master statistic reset. Writing 1 - 247 will reset statistic data for that ID. Writing 1000 will reset the data for all the IDs. | 1 | 0 to 247, 1000 | C3 | SHORT | MB TCP Master statistic reset. 1 to 247 - Reset the statistics of particular ID 100 - Reset statistics of all IDs It resets to 0 once process is completed. | NV | No | R/W | - | 0 | 1000 | 0
|  | 48753 | Reserved | 8
|  | 48761 | Reserved for Debug | 40 |  |  | FLOAT
MB RTU Slave
| MBRTUSlvReset | 48801 | MB_RTU_Slave statistic reset. Writing 1 - 247 will reset statistic data for that ID. Writing 1000 will reset the data for all the IDs. | 1 | 0 to 247, 1000 | C3 | SHORT | MB RTU Slave statistic reset. 1 to 247 - Reset the statistics of particular ID 100 - Reset statistics of all IDs It resets to 0 once process is completed. | NV | No | R/W | - | 0 | 1000 | 0
|  | 48802 | Reserved | 49
Message Logger
| CfgAllOn | 48851 | Configuration for "All Module On" | 1 | - | C3 | Binary | Bit-16 to 8 are Don’t care. Bit 7 = Console Bit 6 = Log file Bit 5 = TCP Bit 4 = Critical Error Bit 3 = Error Bit 2 = warning Bit 1 = Info Bit 0 = Debug. Bit Value = 1 Enable the logging = 0 Disable the logging | NV | No | R/W | - | - | - | -
|  | 48852 | Reserved | 1
| CfgRTUKernalOn | 48853 | Same as 8851 for RTU_Kernel | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
| CfgMsgLgrOn | 48854 | same as 8851 for Message Logger | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
| CfgAlmMngrOn | 48855 | same as 8851 for Alarm Manager | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
| CfgDtLgrOn | 48856 | same as 8851 for Data Logger | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
| CfgMBDtAcqtnOn | 48857 | Same as 8851 for Data Acquisition | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
| CfgMBRTUMstrOn | 48858 | Same as 8851 for MB RTU Master | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
| CfgMBRTUSlvOn | 48859 | Same as 8851 for MB RTU Slave | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
| CfgMBTCPMstrOn | 48860 | Same as 8851 for MB TCP Master | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
| CfgMBTCPSlvOn | 48861 | Same as 8851 for MB TCP Slave | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
|  | 48862 | Reserved for Debug | 4 |  |  | Binary
| CfgWebSvrOn | 48866 | Same as 8851 for Web Server | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
| CfgWetGDtctnOn | 48867 | Same as 8851 for Wet Gas Detection | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
|  | 48868 | Reserved for Debug | 1 |  |  | Binary
| CfgIsaGRAFOn | 48869 | Same as 8851 for IsaGRAF | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
|  | 48870 | Reserved for Debug | 1 |  |  | Binary
| CfgAGAOn | 48871 | Same as 8851 for AGA | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
|  | 48872 | Reserved for Debug | 2 |  |  | Binary
| CfgDNP3SlvOn | 48874 | Same as 8851 for DNP3 Slave | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
| CfgDNP3MstrOn | 48875 | Same as 8851 for DNP3 Master | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
|  | 48876 | Reserved for Debug | 2 |  |  | Binary
| CfgWMPOn | 48878 | Same as 8851 for WMP | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
|  | 48879 | Reserved for Debug | 1 |  |  | Binary
| CfgEnrnMBSlvOn | 48880 | Same as 8851 for Enron MB Slave | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
|  | 48881 | Reserved for Debug | 3 |  |  | Binary
| CfgEthIPOn | 48884 | Same as 8851 for Ethernet IP | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | - | - | -
|  | 48885 | Reserved for Debug | 3 |  |  | Binary
| CfgMBDtCpyOn | 48888 | Same as 8851 for MB Data Copier | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
| CfgBOMOn | 48889 | Same as 8851 for Black Oil Model | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
| CfgMQTTCliAOn | 48890 | Same as 8851 for MQTT Client A | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
| CfgMQTTCliBOn | 48891 | Same as 8851 for MQTT Client B | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
| CfgLcnsMngrOn | 48892 | Same as 8851 for License Manager | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
| CfgPrvsngOn | 48893 | Same as 8851 for Provisioning | 1 | 0 or 1 | C3 | Binary | - | NV | No | R/W | - | 0 | 1 | 0
|  | 48894 | Reserved | 7
|  | Alarm Manager | [10 empty] | - | - | -
| LoAlmSPAI1 | 48901 | Low setpoint Alarm Value for Analog Input channel 1 | 2 | - | C3 | FLOAT | - | NV | No | R/W | - | - | - | -
| HiAlmSPAI1 | 48903 | High setpoint Alarm value for Analog Input channel 1 | 2 | - | C3 | FLOAT | - | NV | No | R/W | - | - | - | -
| LoAlmSPAI2, LoAlmSPAI10 HiAlmSPAI2, HiAlmSPAI10 | 48905 | Low and High setpoint Alarm Value for Analog Input channels 2 to 10 | 36 | - | C3 | FLOAT | - | NV | No | R/W | - | - | - | -
|  | 48941 | Reserved | 60
3rd Party Slave
|  | 49001 | Reserved for 3rd Party Slave | 1000
Black Oil Model
| FactoryResetBOMDt | 410001 | Pre set data to default. Like Factory Reset. | 1 | 0 or 1 | C3 | SHORT |  | NV | No | R/W |  | 0 | 1 | 0
| BOMCalcnTm | 410002 | How often BOM engine is run. | 1 | 1 to 32700 | C3 | SHORT |  | NV | No | R/W | Min | 1 | 32700 | 1
| BOMScanTm | 410003 | Delay between manual trigger and actual BOM engine run. | 1 | 1 to 32700 | C3 | SHORT |  | NV | No | R/W | Min | 1 | 32700 | 1
| TPCh | 410004 | Tubing Pressure Analog Channel | 1 | 1 to 8 | C3 | SHORT | Analog Input 1 to Analog Input 8 | NV | No | R/W |  | 1 | 8 | 1
| TTempCh | 410005 | Tubing Temperature Analog Channel | 1 | 1 to 8 | C3 | SHORT | Analog Input 1 to Analog Input 8 | NV | No | R/W |  | 1 | 8 | 2
| AdTrig | 410006 | Switch BOM calculation from manual to cyclic. | 1 | 0 or 1 | C3 | SHORT |  | NV | No | R/W |  | 0 | 1 | 0
| UserInp | 410007 | Switch live inputs from AI channels to user defined. | 1 | 1 to 3 | C3 | SHORT | Read Head Pressure and Temperature input from: 1 - Static Web Input 2 - Analog Channel 3 - HR or IR | NV | No | R/W |  | 1 | 3 | 1
| BOMEngTrgr | 410008 | Set this register to trigger BOM engine calculation. | 1 | 0 or 1 | C3 | SHORT | 1 - BOM Engine is triggered by HR10008 | NV | No | R/W |  | 0 | 1 | 0
| THdP | 410009 | Tubing Head Pressure | 2 | 3.5 to 950 | C3 | FLOAT |  | NV | No | R/W | psig | 3.5 | 950 | 244
| THdTemp | 410011 | Tubing Head Temperature | 2 | 50 to 250 | C3 | FLOAT |  | NV | No | R/W | deg F | 50 | 250 | 102
| BOMOpertnSts | 410013 | BOM Operation status | 1 | 0 to 3 | C3 | SHORT | BOM Operation Status: 0 - INACTIVE 1 - ACTIVE 2 - ERROR 3 - No License | NV | No | R/W |  | 0 | 3 | 3
| BOMOpertnCntr | 410014 | BOM Engine Operation Counter | 1 |  | C3 | USHORT |  | NV | No | R/W
| BOMOpertnDt | 410015 | BOM Engine Operation Date | 2 |  | C3 | LONG |  | NV | No | R/W | Sec
| BOMOpertnTm | 410017 | BOM Engine Operation Time | 2 |  | C3 | LONG |  | NV | No | R/W | Sec
| TPAd | 410019 | Tubing Pressure Register Address | 1 | 1 to 65535 | C3 | USHORT | THP Address | NV | No | R/W |  | 1 | 65535 | 1
| TPMBRng | 410020 | THP Modbus Range Specifier | 1 | 3,4 |  | USHORT | THP Modbus Range Specifier 3 - HR 4 - IR |  | No | R/W |  | 3 | 4 | 3
| TTempAd | 410021 | Tubing Temperature Register Address | 1 | 1 to 65535 | C3 | USHORT | THT Address | NV | No | R/W |  | 1 | 65535 | 1
| TTMBRng | 410022 | THT Modbus Range Specifier | 1 | 3,4 |  | USHORT | THT Modbus Range Specifier 3 - HR 4 - IR |  | No | R/W |  | 3 | 4 | 3
| TPDtInvs | 410023 | Tubing Pressure Data Inverse | 1 | 0 or 1 | C3 | SHORT |  | NV | No | R/W |  | 0 | 1 | 0
| TTempDtInvs | 410024 | Tubing Temperature Data Inverse | 1 | 0 or 1 | C3 | SHORT |  | NV | No | R/W |  | 0 | 1 | 0
| MBID | 410025 | Modbus ID for Tubing Head Pressure or Temperature | 1 |  | C3 | SHORT |  | NV | No | R/W |  | 1 | 247 | 1
| WellTyp | 410026 | Well type selection | 1 | 1 to 5 | C3 | SHORT | Type of Well: 1 - Gas Lift Well 2 - ESP Well 3 - Natural Flow Well 4 - PCP Well 5 - Sucker Rod Pump Well | NV | No | R/W |  | 1 | 5 | 1
| AssaysDtbs | 410027 | Assays Database | 1 | 1 to 37 | C3 | SHORT |  | NV | No | R/W |  | 1 | 37 | 32
| DtbsTotal | 410028 | Number of Assay Databases | 1 |  | C3 | SHORT |  | NV | No | R/W |  |  |  | 37
| API | 410029 | API | 2 | 16 to 42 | C3 | FLOAT |  | NV | No | R/W | degree | 16 | 42 | 39.7
| GORatio | 410031 | Gas to Oil Ratio (scf/bbl) | 2 | 70 to 11739 | C3 | FLOAT |  | NV | No | R/W | scf/bbl | 70 | 11739 | 477
| WellID | 410033 | Well Identification | 1 | 1 to 32767 | C3 | SHORT |  | NV | No | R/W |  | 1 | 32767 | 20
| WellNum | 410034 | Well Number | 1 | 1 to 32767 | C3 | SHORT |  | NV | No | R/W |  | 1 | 32767 | 1
| WellCfgStup | 410035 | Well Configuration Setup(Configuration choice) [4,0,or 2] | 1 | 1 to 5 | C3 | SHORT | 1 - No Tubing 2 - Tubing Gas Injection 3 - Blocked Tubing 4 - Annular Gas Injection 5 - Solely Tubing Production | NV | No | R/W |  | 1 | 5 | 4
| TelescopeC | 410036 | Is Casing Telescopic (yes/no) | 1 | 0 or 1 | C3 | SHORT |  | NV | No | R/W |  | 0 | 1 | 0
| CVertD | 410037 | Casing Vertical Depth | 2 | 0 to 20000 | C3 | FLOAT |  | NV | No | R/W | feet | 0 | 20000 | 3037
| CInsdDia | 410039 | Casing Inside Diameter | 2 | 0 to 30 | C3 | FLOAT |  | NV | No | R/W | inches | 0 | 30 | 6.184
| CVertD_2 | 410041 | Casing Vertical Depth (only Telescopic casing) | 2 | 0 to 20000 | C3 | FLOAT |  | NV | No | R/W | feet | 0 | 20000 | 0
| CInsdDia_2 | 410043 | Casing Inside Diameter (only Telescopic casing) | 2 | 0 to 30 | C3 | FLOAT |  | NV | No | R/W | inches | 0 | 30 | 0
| CVertD_3 | 410045 | Casing Vertical Depth (only Telescopic casing) | 2 | 0 to 20000 | C3 | FLOAT |  | NV | No | R/W | feet | 0 | 20000 | 0
| CInsdDia_3 | 410047 | Casing Inside Diameter (only Telescopic casing) | 2 | 0 to 30 | C3 | FLOAT |  | NV | No | R/W | inches | 0 | 30 | 0
| CVertD_4 | 410049 | Casing Vertical Depth (only Telescopic casing) | 2 | 0 to 20000 | C3 | FLOAT |  | NV | No | R/W | feet | 0 | 20000 | 0
| CInsdDia_4 | 410051 | Casing Inside Diameter (only Telescopic casing) | 2 | 0 to 30 | C3 | FLOAT |  | NV | No | R/W | inches | 0 | 30 | 0
| CVertD_5 | 410053 | Casing Vertical Depth (only Telescopic casing) | 2 | 0 to 20000 | C3 | FLOAT |  | NV | No | R/W | feet | 0 | 20000 | 0
| CInsdDia_5 | 410055 | Casing Inside Diameter (only Telescopic casing) | 2 | 0 to 30 | C3 | FLOAT |  | NV | No | R/W | inches | 0 | 30 | 0
| TVertD | 410057 | Tubing Vertical Depth | 2 | 0 to 20000 | C3 | FLOAT |  | NV | No | R/W | feet | 0 | 20000 | 2467
| TInsDia | 410059 | Tubing Inside Diameter | 2 | 0 to 10 | C3 | FLOAT |  | NV | No | R/W | inches | 0 | 10 | 2.25
| TThkns | 410061 | Tubing Thickness | 2 | 0.05 to 0.5 | C3 | FLOAT |  | NV | No | R/W | inches | 0.05 | 0.5 | 0.217
| WellInclineVert | 410063 | Well Incline From Vertical | 2 | 0 to 90 | C3 | FLOAT |  | NV | No | R/W | degree | 0 | 90 | 35.7
| TInnerDia | 410065 | Tubing inner diameter | 2 | 0 to 10 | C3 | FLOAT |  | NV | No | R/W | inches | 0 | 10 | 2.5
| CInnerDia | 410067 | Casing Inner diameter | 2 | 0 to 30 | C3 | FLOAT |  | NV | No | R/W | inches | 0 | 30 | 7
| Reserved | 410069 | Reserved | 12 |  |  | FLOAT
| GInjtnLoctn | 410081 | Gas Injection Location (into the annulus or tubing)? | 1 | 1 or 2 | C3 | SHORT | 1 - Annulus 2 - Tubing | NV | No | R/W |  | 1 | 2 | 1
| GInjtnMthd | 410082 | Gas Injection Method Gas Injection Rate or Orifice Pressure Drop(Orifice delta P)? | 1 | 1 or 2 | C3 | SHORT | 1 - Orifice Delta Pressure 2 - Gas Injection Rate | NV | No | R/W |  | 1 | 2 | 2
| FrctnEffGInjtnCmprs | 410083 | Fractional efficiency for gas injection compressor | 2 | 0 to 1 | C3 | FLOAT |  | NV | No | R/W | fraction | 0 | 1 | 0.8
| CHdTemp | 410085 | Casing Head Temperature (Into Annulus Or Tubing) | 2 | 50 to 250 | C3 | FLOAT |  | NV | No | R/W | deg F | 50 | 250 | 73
| EqvltGLftChkPLoss | 410087 | Equivalent Gas Lift Choke Pressure Loss (Into Annulus Or Tubing) | 2 | 0 to 1000 | C3 | FLOAT |  | NV | No | R/W | psig | 0 | 1000 | 500
| ChkPLossVlvPLoss | 410089 | Equivalent Gas Lift Valve Pressure Loss (Into Annulus Or Tubing) | 2 | 0 to 1000 | C3 | FLOAT |  | NV | No | R/W | psig | 0 | 1000 | 202
| InjtnGDensStdCndtn | 410091 | Inj. Gas Density At Std Cond (Into Annulus Or Tubing) | 2 | 0.5 to 2 | C3 | FLOAT |  | NV | No | R/W | gram/liter | 0.5 | 2 | 0.8914
| OrfcDia | 410093 | Orifice Diameter (Annulus Only) (Orifice delta P only) | 2 | 0 to 64 | C3 | FLOAT |  | NV | No | R/W | 1/64 ths inches | 0 | 64 | 32
| GInjtnOrfcDeltaP | 410095 | Gas Inj. Orifice Delta P (Annulus Only) (Orifice delta P only) | 2 | 0 to 1000 | C3 | FLOAT |  | NV | No | R/W | inches of water | 0 | 1000 | 100
| GInjtnOrfcCont | 410097 | Gas Inj. Orifice Constant (Annulus Only) (Orifice delta P only) | 2 | 0 to 1 | C3 | FLOAT |  | NV | No | R/W | adim | 0 | 1 | 0.5
| GInjtnTemp | 410099 | Gas Inj. Temperature (Annulus Only) (Orifice delta P only) | 2 | 50 to 250 | C3 | FLOAT |  | NV | No | R/W | deg F | 50 | 250 | 100
| GInjtnDens | 410101 | Gas Inj. Density (Annulus Only) (Orifice delta P only) | 2 | 0.5 to 2 | C3 | FLOAT |  | NV | No | R/W | gram/liter | 0.5 | 2 | 0.65
| GInjtnOrfcDia | 410103 | Gas Inj. Orifice Diameter (Annulus Only) (Orifice delta P only) | 2 | 0 to 200 | C3 | FLOAT |  | NV | No | R/W | millimeters | 0 | 200 | 10
| GInjtnOrfcPipeID | 410105 | Gas Inj. Orifice Pipe Id (Annulus Only) (Orifice delta P only) | 2 | 0 to 10 | C3 | FLOAT |  | NV | No | R/W | inches | 0 | 10 | 2
| UpstrmMnfldP | 410107 | Upstream Manifold Pressure (Annulus Only) (Orifice delta P only) | 2 | 0 to 5000 | C3 | FLOAT |  | NV | No | R/W | psig | 0 | 5000 | 1000
| CHdP | 410109 | Casing Head Pressure (Annulus Only) | 2 | 0 to 1000 | C3 | FLOAT |  | NV | No | R/W | psig | 0 | 1000 | 598
| NumGLftVlv | 410111 | Number Of Gas Lift Valves (Annulus Only) | 2 | 1 to 7 | C3 | FLOAT |  | NV | No | R/W | integer | 1 | 7 | 1
| AvalInletPGInjtnT | 410113 | Available inlet pressure for gas injection into the (tubing) exclusively | 2 | 0 to 5000 | C3 | FLOAT |  | NV | No | R/W | psig | 0 | 5000 | 1000
| InjtnGRatio | 410115 | Inj. Gas Rate (Into Annulus Or Tubing) (Gas Injection Rate only) | 2 | 0 to 100000 | C3 | FLOAT |  | NV | No | R/W | scf/hour | 0 | 100000 | 23487
| PmpD | 410117 | Pump depth | 2 | 0 to 20000 | C3 | FLOAT |  | NV | No | R/W | feet | 0 | 20000 | 5000
| SubmrsPmpBrkHP | 410119 | Submersible pump brake horsepower | 2 | 0 to 10000 | C3 | FLOAT |  | NV | No | R/W | hp | 0 | 10000 | 100
| FrctnPmpEff | 410121 | Fractional pump efficiency | 2 | 0.8 to 0.99 | C3 | FLOAT |  | NV | No | R/W | fraction | 0.8 | 0.99 | 0.8
| PwrPmpMtrTrmnl | 410123 | Power applied to the pump motor terminals | 2 | 0 to 10000 | C3 | FLOAT |  | NV | No | R/W | hp | 0 | 10000 | 100
| FrctnOvrlPmpEff | 410125 | Fractional overall pump efficiency | 2 | 0 to 1 | C3 | FLOAT |  | NV | No | R/W | fraction | 0 | 1 | 0.5
| SpecGrvtyWSaltSand | 410127 | Specific gravity of water/salt/sand mix | 2 | 0 to 10 | C3 | FLOAT |  | NV | No | R/W | gr/cc | 0 | 10 | 1
| WellDyncLftD | 410129 | Well dynamic lift depth | 2 | 0 to 20000 | C3 | FLOAT |  | NV | No | R/W | feet | 0 | 20000 | 1000
| Reserved | 410131 | Reserved | 10 |  |  | FLOAT
| NumWellCalcnInc | 410141 | Number Well Calculation Increments | 1 | 10 to 100 | C3 | SHORT |  | NV | No | R/W | integer | 10 | 100 | 50
| GroundHeatGrdnt | 410142 | Ground Heat Gradient | 2 | 0.01 to 0.05 | C3 | FLOAT |  | NV | No | R/W | deg F/foot | 0.01 | 0.05 | 0.012
| OverallWellHeatXferCoEff | 410144 | Overall Well Heat Transfer Coefficient | 2 | 1 to 10 | C3 | FLOAT |  | NV | No | R/W | btu/sq ft/deg F | 1 | 10 | 5
| OptnlFlHtcCoEffUUA | 410146 | Optional Flow Related Htc Coefficient* | 2 | 0 to 10 | C3 | FLOAT |  | NV | No | R/W |  | 0 | 10 | 0
| OptnlFlHtcCoEffUUB | 410148 | Optional Flow Related Htc Coefficient* | 2 | 0 to 0.5 | C3 | FLOAT |  | NV | No | R/W |  | 0 | 0.5 | 0
| RghnsFctrWellCsg | 410150 | Roughness Factor Well Casing UUA | 2 | 0.00005 to 0.005 | C3 | FLOAT |  | NV | No | R/W |  | 5e-05 | 0.005 | 0.00015
| RghnsFctrWellT | 410152 | Roughness Factor Well Tubing UUB | 2 | 0.00005 to 0.005 | C3 | FLOAT |  | NV | No | R/W |  | 5e-05 | 0.005 | 0.00015
| RghnsFctrFlLn | 410154 | Roughness Factor Flowlines | 2 | 0.00005 to 0.005 | C3 | FLOAT |  | NV | No | R/W |  | 5e-05 | 0.005 | 0.00015
| Reserved | 410156 | Reserved | 5 |  |  | SHORT
| SrfcLn | 410161 | Is surface line modeled as part of Simulation? | 1 | 0 or 1 | C3 | SHORT |  | NV | No | R/W |  | 0 | 1 | 0
| ContPrdctnIndex | 410162 | Constant Productivity Index (Q/PSO-PFO) | 2 | 0 to 100 | C3 | FLOAT |  | NV | No | R/W | bpd/psi | 0 | 100 | 1.38
| AFctr | 410164 | A factor where PI = 1 / (A + B x flowrate). | 2 | 0 to 100 | C3 | FLOAT |  | NV | No | R/W | bpd/psi | 0 | 100 | 0
| BFctr | 410166 | B factor where PI = 1 / (A + B x flowrate). | 2 | 0 to 100 | C3 | FLOAT |  | NV | No | R/W | bpd/psi | 0 | 100 | 0
| StaticResP | 410168 | Static Reservoir Pressure | 2 | 0 to 100000 | C3 | FLOAT |  | NV | No | R/W | psig | 0 | 100000 | 1250
| StaticResTemp | 410170 | Static Reservoir Temperature | 2 | 0 to 1000 | C3 | FLOAT |  | NV | No | R/W | deg F | 0 | 1000 | 194
| TotVolFlR | 410172 | Total volume flow rate at s.t.c. (oil + water) | 2 | 0 to 300000 | C3 | FLOAT |  | NV | No | R/W | bpd | 0 | 300000 | 810
| CnvgncEndP | 410174 | Convergence end pressure (only if surface line is modeled) | 2 | 15 to 10000 | C3 | FLOAT |  | NV | No | R/W | psig | 15 | 10000 | 100
| EndPCh | 410176 | Analog Channel # for Convergence End pressure. | 1 | 1 to 8 | C3 | SHORT | Analog Channel 1 to 8 | NV | No | R/W |  | 1 | 8 | 3
| AIInp | 410177 | Switch between Analog Ch or User defined for Convergence End Pressure. | 1 | 0 or 1 | C3 | SHORT | 0 - Use PEND for convergence End Pressure 1- Use AI for convergence End Pressure | NV | No | R/W |  | 0 | 1 | 0
| Reserved | 410178 | Reserved | 3 |  |  | SHORT
| LqdDensSC | 410181 | Liquid density at s.c. | 2 | 35 to 65 | C3 | FLOAT |  | NV | No | R/W | lbs / cu ft | 35 | 65 | 51.5798
| GORatioSC | 410183 | Gas to oil ratio at s.c. | 2 | 0 to 30000 | C3 | FLOAT |  | NV | No | R/W | scf/stb | 0 | 30000 | 477
| SoltnGDensSC | 410185 | Solution gas density at s.c. | 2 | 0.5 to 2 | C3 | FLOAT |  | NV | No | R/W | grams/lt | 0.5 | 2 | 0.8914
| FreeGAdj | 410187 | Free gas adjustment (formation GOR) | 2 | 0 to 15000 | C3 | FLOAT |  | NV | No | R/W | scf/stb | 0 | 15000 | 966
| FreeGDensSC | 410189 | Free gas density at s.c. | 2 | 0.5 to 2 | C3 | FLOAT |  | NV | No | R/W | grams/lt | 0.5 | 2 | 0.8914
| VolFrctnW | 410191 | Volume Fraction Water | 2 | 0 to 0.98 | C3 | FLOAT |  | NV | No | R/W | fraction | 0 | 0.98 | 0.581
| SalntyWellW | 410193 | Salinity of well water | 2 | 0 to 50 | C3 | FLOAT |  | NV | No | R/W | thou ppm | 0 | 50 | 25.302
| Reserved | 410195 | Reserved | 2 |  | C3 | FLOAT |  | NV | No | R/W
| Reserved | 410197 | Reserved | 2
| Reserved | 410199 | Reserved | 1 |  | C3 | SHORT |  | NV | No | R/W
| Reserved | 410200 | Reserved | 1 |  | C3 | SHORT |  | NV | No | R/W
| AssaysDtbs_CMDM_1_1 | 410201 | Initializing value of 0 (irrelevant) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
| AssaysDtbs_CMDM_2_1 | 410205 | C1 Bubble Point (BPSC) | 4 | -10 to 10000 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 10000 | 643.9528
| AssaysDtbs_CMDM_3_1 | 410209 | C2 Bubble Point (BPSC) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 4.3647
| AssaysDtbs_CMDM_4_1 | 410213 | Temp. value | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 129
| AssaysDtbs_CMDM_5_1 | 410217 | C1 Mixture Density (MDLTF) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0.012596
| AssaysDtbs_CMDM_6_1 | 410221 | C2 Mixture Density (MDLTF) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0.059255
| AssaysDtbs_CMDM_7_1 | 410225 | C3 Mixture Density (MDLTF) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | -1.1e-05
| AssaysDtbs_CMDM_8_1 | 410229 | C4 Mixture Density (MDLTF) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
| AssaysDtbs_CMDM_9_1 | 410233 | Temp. value | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 214
| AssaysDtbs_CMDM_10_1 | 410237 | C1 Mixture Density (MDHTF) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | -0.044706
| AssaysDtbs_CMDM_11_1 | 410241 | C2 Mixture Density (MDHTF) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0.046865
| AssaysDtbs_CMDM_12_1 | 410245 | C3 Mixture Density (MDHTF) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | -1.5e-05
| AssaysDtbs_CMDM_13_1 | 410249 | C4 Mixture Density (MDHTF) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
|  | 410253 | Reserved | 28 |  |  |  |  | NV | No | R/W
| AssaysDtbs_CLVM_1_1 | 410281 | Initializing value of 0 (irrelevant) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
| AssaysDtbs_CLVM_2_1 | 410285 | Temp. value | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 129
| AssaysDtbs_CLVM_3_1 | 410289 | C1 Liquid Viscosity (LVBBLT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0.3953
| AssaysDtbs_CLVM_4_1 | 410293 | C2 Liquid Viscosity (LVBBLT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | -0.001004
| AssaysDtbs_CLVM_5_1 | 410297 | C3 Liquid Viscosity (LVBBLT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 1e-06
| AssaysDtbs_CLVM_6_1 | 410301 | C4 Liquid Viscosity (LVBBLT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
| AssaysDtbs_CLVM_7_1 | 410305 | Temp. value | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 214
| AssaysDtbs_CLVM_8_1 | 410309 | C1 Liquid Viscosity (LVBBHT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0.23317
| AssaysDtbs_CLVM_9_1 | 410313 | C2 Liquid Viscosity (LVBBHT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | -0.000487
| AssaysDtbs_CLVM_10_1 | 410317 | C3 Liquid Viscosity (LVBBHT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
| AssaysDtbs_CLVM_11_1 | 410321 | C4 Liquid Viscosity (LVBBHT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
| AssaysDtbs_CLVM_12_1 | 410325 | C1 Liquid Viscosity (LVABLT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0.083288
| AssaysDtbs_CLVM_13_1 | 410329 | C2 Liquid Viscosity (LVABLT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 8e-06
| AssaysDtbs_CLVM_14_1 | 410333 | C1 Liquid Viscosity (LVABHT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0.029958
| AssaysDtbs_CLVM_15_1 | 410337 | C2 Liquid Viscosity (LVABHT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 1.7e-05
|  | 410341 | Reserved | 20 |  |  |  |  | NV | No | R/W
| AssaysDtbs_CLDM_1_1 | 410361 | Initializing value of 0 (irrelevant) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
| AssaysDtbs_CLDM_2_1 | 410365 | Temp. value | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 129
| AssaysDtbs_CLDM_3_1 | 410369 | C1 Liquid Density (LDBBLT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0.85696
| AssaysDtbs_CLDM_4_1 | 410373 | C2 Liquid Density (LDBBLT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | -0.000214
| AssaysDtbs_CLDM_5_1 | 410377 | C3 Liquid Density (LDBBLT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
| AssaysDtbs_CLDM_6_1 | 410381 | C4 Liquid Density (LDBBLT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
| AssaysDtbs_CLDM_7_1 | 410385 | Temp. value | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 214
| AssaysDtbs_CLDM_8_1 | 410389 | C1 Liquid Density (LDBBHT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0.83254
| AssaysDtbs_CLDM_9_1 | 410393 | C2 Liquid Density (LDBBHT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | -0.000263
| AssaysDtbs_CLDM_10_1 | 410397 | C3 Liquid Density (LDBBHT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
| AssaysDtbs_CLDM_11_1 | 410401 | C4 Liquid Density (LDBBHT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
| AssaysDtbs_CLDM_12_1 | 410405 | C1 Liquid Density (LDABLTD) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 44.5975
| AssaysDtbs_CLDM_13_1 | 410409 | C2 Liquid Density (LDABLTD) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0.000228
| AssaysDtbs_CLDM_14_1 | 410413 | C1 Liquid Density (LDABHTD) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 39.3284
| AssaysDtbs_CLDM_15_1 | 410417 | C2 Liquid Density (LDABHTD) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0.002462
|  | 410421 | Reserved | 20 |  |  |  |  | NV | No | R/W
| AssaysDtbs_CGRM_1_1 | 410441 | Initializing value of 0 (irrelevant) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
| AssaysDtbs_CGRM_2_1 | 410445 | C1 Gas-oil Ratio (GRBB) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 298.2482
| AssaysDtbs_CGRM_3_1 | 410449 | C2 Gas-oil Ratio (GRBB) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0.32827
| AssaysDtbs_CGRM_4_1 | 410453 | C3 Gas-oil Ratio (GRBB) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
| AssaysDtbs_CGRM_5_1 | 410457 | C4 Gas-oil Ratio (GRBB) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0.009277
| AssaysDtbs_CGRM_6_1 | 410461 | C5 Gas-oil Ratio (GRBB) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
|  | 410465 | Reserved | 56 |  |  |  |  | NV | No | R/W
| AssaysDtbs_CGDM_1_1 | 410521 | Initializing value of 0 (irrelevant) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
| AssaysDtbs_CGDM_2_1 | 410525 | Temp. value | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 129
| AssaysDtbs_CGDM_3_1 | 410529 | C1 Gas Density (GDLT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 1.0141
| AssaysDtbs_CGDM_4_1 | 410533 | C2 Gas Density (GDLT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
| AssaysDtbs_CGDM_5_1 | 410537 | C3 Gas Density (GDLT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | -0.012478
| AssaysDtbs_CGDM_6_1 | 410541 | C4 Gas Density (GDLT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0.000859
| AssaysDtbs_CGDM_7_1 | 410545 | Temp. value | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 214
| AssaysDtbs_CGDM_8_1 | 410549 | C1 Gas Density (GDHT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 1.1427
| AssaysDtbs_CGDM_9_1 | 410553 | C2 Gas Density (GDHT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0
| AssaysDtbs_CGDM_10_1 | 410557 | C3 Gas Density (GDHT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | -0.02588
| AssaysDtbs_CGDM_11_1 | 410561 | C4 Gas Density (GDHT) | 4 | -10 to 500 | C3 | DOUBLE |  | NV | No | R/W |  | -10 | 500 | 0.00244
|  | 410565 | Reserved | 36 |  |  |  |  | NV | No | R/W
|  | 410601 | New Assay Database | 402 | [5 empty] | No
| BOMPMsrmnt[0] | 411003 | Pressure Measurement Point 1 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[1] | 411005 | Pressure Measurement Point 2 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[2] | 411007 | Pressure Mesaurement Point 3 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[3] | 411009 | Pressure Measurement Point 4 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[4] | 411011 | Pressure Measurement Point 5 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[5] | 411013 | Pressure Measurement Point 6 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[6] | 411015 | Pressure Measurement Point 7 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[7] | 411017 | Pressure Measurement Point 8 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[8] | 411019 | Pressure Measurement Point 9 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[9] | 411021 | Pressure Measurement Point 10 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[10] | 411023 | Pressure Measurement Point 11 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[11] | 411025 | Pressure Measurement Point 12 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[12] | 411027 | Pressure Measurement Point 13 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[13] | 411029 | Pressure Measurement Point 14 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[14] | 411031 | Pressure Measurement Point 15 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[15] | 411033 | Pressure Measurement Point 16 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[16] | 411035 | Pressure Measurement Point 17 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[17] | 411037 | Pressure Measurement Point 18 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[18] | 411039 | Pressure Measurement Point 19 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[19] | 411041 | Pressure Measurement Point 20 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[20] | 411043 | Pressure Measurement Point 21 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[21] | 411045 | Pressure Measurement Point 22 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[22] | 411047 | Pressure Measurement Point 23 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[23] | 411049 | Pressure Measurement Point 24 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[24] | 411051 | Pressure Measurement Point 25 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[25] | 411053 | Pressure Measurement Point 26 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[26] | 411055 | Pressure Measurement Point 27 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[27] | 411057 | Pressure Measurement Point 28 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[28] | 411059 | Pressure Measurement Point 29 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[29] | 411061 | Pressure Measurement Point 30 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[30] | 411063 | Pressure Measurement Point 31 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[31] | 411065 | Pressure Measurement Point 32 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[32] | 411067 | Pressure Measurement Point 33 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[33] | 411069 | Pressure Measurement Point 34 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[34] | 411071 | Pressure Measurement Point 35 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[35] | 411073 | Pressure Measurement Point 36 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[36] | 411075 | Pressure Measurement Point 37 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[37] | 411077 | Pressure Measurement Point 38 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[38] | 411079 | Pressure Measurement Point 39 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[39] | 411081 | Pressure Measurement Point 40 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[40] | 411083 | Pressure Measurement Point 41 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[41] | 411085 | Pressure Measurement Point 42 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[42] | 411087 | Pressure Measurement Point 43 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[43] | 411089 | Pressure Measurement Point 44 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[44] | 411091 | Pressure Measurement Point 45 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[45] | 411093 | Pressure Measurement Point 46 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[46] | 411095 | Pressure Measurement Point 47 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[47] | 411097 | Pressure Measurement Point 48 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[48] | 411099 | Pressure Measurement Point 49 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMPMsrmnt[49] | 411101 | Pressure Measurement Point 50 | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMTempMsrmnt[0] | 411103 | Temperature Measurement Point 1 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[1] | 411105 | Temperature Measurement Point 2 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[2] | 411107 | Temperature Measurement Point 3 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[3] | 411109 | Temperature Measurement Point 4 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[4] | 411111 | Temperature Measurement Point 5 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[5] | 411113 | Temperature Measurement Point 6 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[6] | 411115 | Temperature Measurement Point 7 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[7] | 411117 | Temperature Measurement Point 8 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[8] | 411119 | Temperature Measurement Point 9 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[9] | 411121 | Temperature Measurement Point 10 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[10] | 411123 | Temperature Measurement Point 11 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[11] | 411125 | Temperature Measurement Point 12 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[12] | 411127 | Temperature Measurement Point 13 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[13] | 411129 | Temperature Measurement Point 14 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[14] | 411131 | Temperature Measurement Point 15 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[15] | 411133 | Temperature Measurement Point 16 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[16] | 411135 | Temperature Measurement Point 17 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[17] | 411137 | Temperature Measurement Point 18 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[18] | 411139 | Temperature Measurement Point 19 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[19] | 411141 | Temperature Measurement Point 20 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[20] | 411143 | Temperature Measurement Point 21 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[21] | 411145 | Temperature Measurement Point 22 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[22] | 411147 | Temperature Measurement Point 23 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[23] | 411149 | Temperature Measurement Point 24 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[24] | 411151 | Temperature Measurement Point 25 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[25] | 411153 | Temperature Measurement Point 26 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[26] | 411155 | Temperature Measurement Point 27 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[27] | 411157 | Temperature Measurement Point 28 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[28] | 411159 | Temperature Measurement Point 29 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[29] | 411161 | Temperature Measurement Point 30 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[30] | 411163 | Temperature Measurement Point 31 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[31] | 411165 | Temperature Measurement Point 32 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[32] | 411167 | Temperature Measurement Point 33 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[33] | 411169 | Temperature Measurement Point 34 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[34] | 411171 | Temperature Measurement Point 35 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[35] | 411173 | Temperature Measurement Point 36 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[36] | 411175 | Temperature Measurement Point 37 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[37] | 411177 | Temperature Measurement Point 38 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[38] | 411179 | Temperature Measurement Point 39 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[39] | 411181 | Temperature Measurement Point 40 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[40] | 411183 | Temperature Measurement Point 41 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[41] | 411185 | Temperature Measurement Point 42 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[42] | 411187 | Temperature Measurement Point 43 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[43] | 411189 | Temperature Measurement Point 44 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[44] | 411191 | Temperature Measurement Point 45 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[45] | 411193 | Temperature Measurement Point 46 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[46] | 411195 | Temperature Measurement Point 47 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[47] | 411197 | Temperature Measurement Point 48 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[48] | 411199 | Temperature Measurement Point 49 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMTempMsrmnt[49] | 411201 | Temperature Measurement Point 50 | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMDMsrmnt[0] | 411203 | Depth Measurement Point 1 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[1] | 411205 | Depth Measurement Point 2 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[2] | 411207 | Depth Measurement Point 3 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[3] | 411209 | Depth Measurement Point 4 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[4] | 411211 | Depth Measurement Point 5 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[5] | 411213 | Depth Measurement Point 6 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[6] | 411215 | Depth Measurement Point 7 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[7] | 411217 | Depth Measurement Point 8 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[8] | 411219 | Depth Measurement Point 9 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[9] | 411221 | Depth Measurement Point 10 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[10] | 411223 | Depth Measurement Point 11 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[11] | 411225 | Depth Measurement Point 12 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[12] | 411227 | Depth Measurement Point 13 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[13] | 411229 | Depth Measurement Point 14 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[14] | 411231 | Depth Measurement Point 15 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[15] | 411233 | Depth Measurement Point 16 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[16] | 411235 | Depth Measurement Point 17 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[17] | 411237 | Depth Measurement Point 18 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[18] | 411239 | Depth Measurement Point 19 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[19] | 411241 | Depth Measurement Point 20 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[20] | 411243 | Depth Measurement Point 21 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[21] | 411245 | Depth Measurement Point 22 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[22] | 411247 | Depth Measurement Point 23 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[23] | 411249 | Depth Measurement Point 24 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[24] | 411251 | Depth Measurement Point 25 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[25] | 411253 | Depth Measurement Point 26 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[26] | 411255 | Depth Measurement Point 27 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[27] | 411257 | Depth Measurement Point 28 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[28] | 411259 | Depth Measurement Point 29 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[29] | 411261 | Depth Measurement Point 30 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[30] | 411263 | Depth Measurement Point 31 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[31] | 411265 | Depth Measurement Point 32 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[32] | 411267 | Depth Measurement Point 33 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[33] | 411269 | Depth Measurement Point 34 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[34] | 411271 | Depth Measurement Point 35 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[35] | 411273 | Depth Measurement Point 36 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[36] | 411275 | Depth Measurement Point 37 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[37] | 411277 | Depth Measurement Point 38 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[38] | 411279 | Depth Measurement Point 39 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[39] | 411281 | Depth Measurement Point 40 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[40] | 411283 | Depth Measurement Point 41 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[41] | 411285 | Depth Measurement Point 42 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[42] | 411287 | Depth Measurement Point 43 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[43] | 411289 | Depth Measurement Point 44 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[44] | 411291 | Depth Measurement Point 45 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[45] | 411293 | Depth Measurement Point 46 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[46] | 411295 | Depth Measurement Point 47 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[47] | 411297 | Depth Measurement Point 48 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[48] | 411299 | Depth Measurement Point 49 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDMsrmnt[49] | 411301 | Depth Measurement Point 50 | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMFlMsrmnt[0] | 411303 | Flow Measurement Point 1 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[1] | 411304 | Flow Measurement Point 2 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[2] | 411305 | Flow Measurement Point 3 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[3] | 411306 | Flow Measurement Point 4 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[4] | 411307 | Flow Measurement Point 5 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[5] | 411308 | Flow Measurement Point 6 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[6] | 411309 | Flow Measurement Point 7 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[7] | 411310 | Flow Measurement Point 8 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[8] | 411311 | Flow Measurement Point 9 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[9] | 411312 | Flow Measurement Point 10 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[10] | 411313 | Flow Measurement Point 11 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[11] | 411314 | Flow Measurement Point 12 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[12] | 411315 | Flow Measurement Point 13 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[13] | 411316 | Flow Measurement Point 14 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[14] | 411317 | Flow Measurement Point 15 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[15] | 411318 | Flow Measurement Point 16 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[16] | 411319 | Flow Measurement Point 17 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[17] | 411320 | Flow Measurement Point 18 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[18] | 411321 | Flow Measurement Point 19 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[19] | 411322 | Flow Measurement Point 20 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[20] | 411323 | Flow Measurement Point 21 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[21] | 411324 | Flow Measurement Point 22 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[22] | 411325 | Flow Measurement Point 23 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[23] | 411326 | Flow Measurement Point 24 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[24] | 411327 | Flow Measurement Point 25 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[25] | 411328 | Flow Measurement Point 26 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[26] | 411329 | Flow Measurement Point 27 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[27] | 411330 | Flow Measurement Point 28 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[28] | 411331 | Flow Measurement Point 29 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[29] | 411332 | Flow Measurement Point 30 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[30] | 411333 | Flow Measurement Point 31 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[31] | 411334 | Flow Measurement Point 32 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[32] | 411335 | Flow Measurement Point 33 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[33] | 411336 | Flow Measurement Point 34 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[34] | 411337 | Flow Measurement Point 35 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[35] | 411338 | Flow Measurement Point 36 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[36] | 411339 | Flow Measurement Point 37 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[37] | 411340 | Flow Measurement Point 38 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[38] | 411341 | Flow Measurement Point 39 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[39] | 411342 | Flow Measurement Point 40 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[40] | 411343 | Flow Measurement Point 41 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[41] | 411344 | Flow Measurement Point 42 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[42] | 411345 | Flow Measurement Point 43 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[43] | 411346 | Flow Measurement Point 44 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[44] | 411347 | Flow Measurement Point 45 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[45] | 411348 | Flow Measurement Point 46 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[46] | 411349 | Flow Measurement Point 47 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[47] | 411350 | Flow Measurement Point 48 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[48] | 411351 | Flow Measurement Point 49 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMFlMsrmnt[49] | 411352 | Flow Measurement Point 50 | 1 | 0 to 4 | C3 | USHORT | 1 - BUBL 2 - SLUG 3 - FROT 4 - RIPL | NV | No | R/W |  | 0 | 4 | 0
| BOMBtmHTemp | 411353 | Flow Bottom Hole Pressure | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMElvtnPDrop | 411355 | Elevation Pressure Drop | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMFrctnPDrop | 411357 | Friction Pressure Drop | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMFitPDrop | 411359 | Fittings pressure Drop | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMTotPDrop | 411361 | Total Pressure Drop | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMWellHdP | 411363 | Wellhead Pressure | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMWellHdTemp | 411365 | Wellhead Temperature | 2 |  | C3 | FLOAT |  | NV | No | R/W | deg F
| BOMOMassFlR | 411367 | Oil Mass Flow Rate | 2 |  | C3 | FLOAT |  | NV | No | R/W | lbs/sec
| BOMGMassFlR | 411369 | Gas Mass Flow Rate | 2 |  | C3 | FLOAT |  | NV | No | R/W | lbs/sec
| BOMWMassFlR | 411371 | Water Mass Flow Rate | 2 |  | C3 | FLOAT |  | NV | No | R/W | lbs/sec
| BOMTotMassFlR | 411373 | Total Mass Flow Rate | 2 |  | C3 | FLOAT |  | NV | No | R/W | lbs/sec
| BOMWFlR | 411375 | Water Flow Rate | 2 |  | C3 | FLOAT |  | NV | No | R/W | bpd
| BOMOFlR | 411377 | Oil Flow Rate | 2 |  | C3 | FLOAT |  | NV | No | R/W | bpd
| BOMInjtnGR | 411379 | Inject Gas Rate | 2 |  | C3 | FLOAT |  | NV | No | R/W | scf/hr
| BOMFrmtnGR | 411381 | Formation Gas Rate | 2 |  | C3 | FLOAT |  | NV | No | R/W | scf/hr
| BOMAssctdGR | 411383 | Associated Gas Rate | 2 |  | C3 | FLOAT |  | NV | No | R/W | scf/hr
| BOMTotExitG | 411385 | Total Exit Gas | 2 |  | C3 | FLOAT |  | NV | No | R/W | scf/hr
| BOMSpecGFl | 411387 | Specified Gas Flow | 2 |  | C3 | FLOAT |  | NV | No | R/W | scf/hr
| BOMCalcMallFlR | 411389 | Calculated Mass Flow Rate | 2 |  | C3 | FLOAT |  | NV | No | R/W | lbs/sec
| BOMGInjtnFrctnFctr | 411391 | Gas Injection Friction factor | 2 |  | C3 | FLOAT |  | NV | No | R/W
| BOMReynoldsNum | 411393 | Reynolds Number | 2 |  | C3 | FLOAT |  | NV | No | R/W
| BOMGVscty | 411395 | Gas Viscosity | 2 |  | C3 | FLOAT |  | NV | No | R/W | centipoise
| BOMPmpDeltaP | 411397 | Pump Delta P Boost | 2 |  | C3 | FLOAT |  | NV | No | R/W | psig
| BOMSubmrsPmpLocD | 411399 | Submersible Pump Location Depth | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMDensPmpFld | 411401 | Density of Pump Fluid | 2 |  | C3 | FLOAT |  | NV | No | R/W | pcf
| BOMPmpFldVolFrctn | 411403 | Pump Fluid Formation Volume Fraction | 2 |  | C3 | FLOAT |  | NV | No | R/W
| BOMPmpBrkHP | 411405 | Pump Brake Horsepower | 2 |  | C3 | FLOAT |  | NV | No | R/W | hp
| BOMPmpOFlR | 411407 | Pump Oil Flow Rate | 2 |  | C3 | FLOAT |  | NV | No | R/W | bpd
| BOMPmpEff | 411409 | Pump Efficiency | 2 |  | C3 | FLOAT |  | NV | No | R/W | fraction
| BOMPmpMtrHP | 411411 | Horsepower Applied to Pump Motor | 2 |  | C3 | FLOAT |  | NV | No | R/W | hp
| BOMPmpDyncLftD | 411413 | Pump Dynamic Lift Depth | 2 |  | C3 | FLOAT |  | NV | No | R/W | feet
| BOMPmpFldODens | 411415 | Pump Fluid oil Density | 2 |  | C3 | FLOAT |  | NV | No | R/W | pcf
| BOMWCt | 411417 | Water Cut | 2 |  | C3 | FLOAT |  | NV | No | R/W | fraction
| BOMWSpecGrvty | 411419 | Specific Gravity of Water | 2 |  | C3 | FLOAT |  | NV | No | R/W | gm/l
| BOMFldLftSpecGrvty | 411421 | Specific Gravity of Fluid Lift | 2 |  | C3 | FLOAT |  | NV | No | R/W | gm/l
|  | 411423 | Reserved | 578
|  | 412001 | Reserved for iNOC | 2200
Wet Gas Detection
| AlgoTrgrTm | 414201 | Algorithm Trigger Time | 2 | 1 to 86400 | C3 | LONG | This is the time after which algorithm will be triggered to do the calculation | NV | No | R/W | Sec | 1 | 86400 | 2
| MBScanTm | 414203 | MB Scan Time | 2 | 1 to 86400 | C3 | LONG | This is the time after which modbus registers will be scanned to check any configuration value is changed or not | NV | No | R/W | Sec | 1 | 86400 | 1
| VenturiPipeDia | 414205 | Venturi Pipe Diameter | 2 | 0 to 10000 | C3 | FLOAT | Venturi Pipe Diameter | NV | No | R/W | mm | 0 | 10000 | 154.051
| VenturiThrtDia | 414207 | Venturi Throat Diameter | 2 | 0 to 10000 | C3 | FLOAT | Venturi Throat Diameter | NV | No | R/W | mm | 0 | 10000 | 112.236
| VenturiCoEffDisch | 414209 | Venturi Coefficient of Disch | 2 | -100 to 100 | C3 | FLOAT | Venturi Coefficient of Disch | NV | No | R/W |  | -100 | 100 | 0.995
| VenturiRefTemp | 414211 | Venturi Reference Temperature | 2 | -100 to 1000 | C3 | FLOAT | Venturi Reference Temperature | NV | No | R/W | Deg C | -100 | 1000 | 15
| ThrmlExpnsnCoEff | 414213 | Thermal Expansion Coefficient X 10-6 | 2 | -10 to 10 | C3 | FLOAT | Thermal Expansion Coefficient X 10-6 | NV | No | R/W | C | -10 | 10 | 1.27e-05
| GMolclrWtSTP | 414215 | Gas Molecular Weight at STP | 2 | 0 to 1000 | C3 | FLOAT | Gas Molecular Weight at STP | NV | No | R/W | kg/kgmol | 0 | 1000 | 20.441
| PseudoCrtclPSTP | 414217 | Pseudo Critical Pressure at STP | 2 | 0 to 100000 | C3 | FLOAT | Pseudo Critical Pressure at STP | NV | No | R/W | kPa | 0 | 100000 | 4563
| PseudoCrtclTempSTP | 414219 | Pseudo Critical Temperature at STP | 2 | 0 to 1000 | C3 | FLOAT | Pseudo Critical Temperature at STP | NV | No | R/W | K | 0 | 1000 | 213
| RatioSpecHeatVenturiMatrl | 414221 | Ratio of Specific Heat of Venturi Material | 2 | 0 to 100 | C3 | FLOAT | Ratio of Specific Heat of Venturi Material | NV | No | R/W |  | 0 | 100 | 1.173
| CndnstDens | 414223 | Condensate Density | 2 | 0 to 10000 | C3 | FLOAT | Condensate Density | NV | No | R/W | kg/m3 | 0 | 10000 | 802
| CndnstMolclrWt | 414225 | Condensate Molecular Weight | 2 | 0 to 1000 | C3 | FLOAT | Condensate Molecular Weight | NV | No | R/W | kg/kgmol | 0 | 1000 | 147.5
| WDensSTP | 414227 | Water Density at STP | 2 | 0 to 10000 | C3 | FLOAT | Water Density at STP | NV | No | R/W | kg/m3 | 0 | 10000 | 1060
| CndnstGRatioSTP | 414229 | Condensate Gas Ratio at STP | 2 | -10000 to 10000 | C3 | FLOAT | Condensate Gas Ratio at STP | NV | No | R/W | m3/e6sm3 | -10000 | 10000 | 450
| WGRatioSTP | 414231 | Water Gas Ratio at STP | 2 | 0 to 100 | C3 | FLOAT | Water Gas Ratio at STP | NV | No | R/W | m3/e6sm3 | 0 | 100 | 15
| APrtlPH20Crln | 414233 | Partial Pressure H2O Correlation [APPH2O] | 2 | -100 to 100 | C3 | FLOAT | A Partial Pressure H20 Correlation | NV | No | R/W | kPa/C^1/3 | -100 | 100 | 0.00030619
| BPrtlPH20Crln | 414235 | Partial Pressure H2O Correlation [BPPH2O] | 2 | -100 to 100 | C3 | FLOAT | B Partial Pressure H20 Correlationt | NV | No | R/W | kPa/C^1/2 | -100 | 100 | -0.038049
| CPrtlPH20Crln | 414237 | Partial Pressure H2O Correlation [CPPH2O] | 2 | -100 to 100 | C3 | FLOAT | C Partial Pressure H20 Correlation | NV | No | R/W | kPa/C | -100 | 100 | 2.1195
| DPrtlPH20Crln | 414239 | Partial Pressure H2O Correlation [DPPH2O] | 2 | -100 to 100 | C3 | FLOAT | D Partial Pressure H20 Correlation | NV | No | R/W | kPa | -100 | 100 | -36.054
| AGPseudoCrtclTempLinrRegsn | 414241 | Gas Pseudo Critical Temperature Linear Regression [ATPC] | 2 | -100 to 100 | C3 | FLOAT | A Gas Pseudo Critical Temperature Linear Regression | NV | No | R/W | K/C | -100 | 100 | 0.0925
| BGPseudoCrtclTempLinrRegsn | 414243 | Gas Pseudo Critical Temperature Linear Regression [BTPC] | 2 | -1000 to 1000 | C3 | FLOAT | B Gas Pseudo Critical Temperature Linear Regression | NV | No | R/W | K | -1000 | 1000 | 201.65
| AGPseudoCrtclPLinrRegsn | 414245 | A Gas Pseudo Critical Pressure Linear Regression [APPC] | 2 | -100 to 100 | C3 | FLOAT | A Gas Pseudo Critical Pressure Linear Regression | NV | No | R/W | kPa/C | -100 | 100 | -0.35
| BGPseudoCrtclPLinrRegsn | 414247 | B Gas Pseudo Critical Pressure Linear Regression [BPPC] | 2 | -10000 to 10000 | C3 | FLOAT | B Gas Pseudo Critical Pressure Linear Regression | NV | No | R/W | kPa | -10000 | 10000 | 4601
| AGMolclrWtLinrRegsn | 414249 | Gas Molecular Weight Linear Regression [AGMW] | 2 | -100 to 100 | C3 | FLOAT | A Gas Molecular Weight Linear Regression | NV | No | R/W | kg/kgmolC | -100 | 100 | 0.019175
| BGMolclrWtLinrRegsn | 414251 | Gas Molecular Weight Linear Regression [BGMW] | 2 | -1000 to 1000 | C3 | FLOAT | B Gas Molecular Weight Linear Regression | NV | No | R/W | kg/kgmol | -1000 | 1000 | 18.282
| ACndnstMolclrWtLinrRegsn | 414253 | Cond Molecular Weight Linear Regression [ACMW] | 2 | -100 to 100 | C3 | FLOAT | A Condensate Molecular Weight Linear Regression | NV | No | R/W | kg/kgmolC | -100 | 100 | 0.3147
| BCndnstMolclrWtLinrRegsn | 414255 | Cond Molecular Weight Linear Regression [BCMW] | 2 | -100 to 100 | C3 | FLOAT | B Condensate Molecular Weight Linear Regression | NV | No | R/W | kg/kgmolkPa | -100 | 100 | -0.00323
| CCndnstMolclrWtLinrRegsn | 414257 | Cond Molecular Weight Linear Regression [CCMW] | 2 | -1000 to 1000 | C3 | FLOAT | C Condensate Molecular Weight Linear Regression | NV | No | R/W | kg/kgmol | -1000 | 1000 | 94.57
| ACndnstDensLinrRegsn | 414259 | Cond Density Linear Regression T [ARHOC] | 2 | -100 to 100 | C3 | FLOAT | A Condensate Density Linear Regression | NV | No | R/W | kg/m3C | -100 | 100 | 0.2457
| BCndnstDensLinrRegsn | 414261 | Cond Density Linear Regression P [BRHOC] | 2 | -100 to 100 | C3 | FLOAT | B Condensate Density Linear Regressiont | NV | No | R/W | kg/m3kPa | -100 | 100 | -0.005853
| CCndnstDensLinrRegsn | 414263 | Cond Density Linear Regression TP [CRHOC] | 2 | -100 to 100 | C3 | FLOAT | C Condensate Density Linear Regression | NV | No | R/W | kg/m3kPaC | -100 | 100 | 0
| DCndnstDensLinrRegsn | 414265 | Cond Density Linear Regression T [DRHOC] | 2 | -10000 to 10000 | C3 | FLOAT | D Condensate Density Linear Regression | NV | No | R/W | kg/m3 | -10000 | 10000 | 706.552
| AWVaporGCrln | 414267 | Water Vapour in Gas Correlation [AWVGRS] | 2 | -100 to 100 | C3 | FLOAT | Water Vapour in Gas Correlation | NV | No | R/W |  | -100 | 100 | 2.5129
| BWGCrln | 414269 | Water in Gas Correlation [BWVGRS] | 2 | -100 to 100 | C3 | FLOAT | Water in Gas Correlation | NV | No | R/W |  | -100 | 100 | -4.0259
| UpstrmPDeviceID | 414271 | Upstream Pressure Device ID | 1 | -1, 1 to 247 | C3 | USHORT | Upstream Pressure Device ID | NV | No | R/W |  | -1 | 247 | 1
| UpstrmPAd | 414272 | Upstream Pressure Address | 1 | 1 to 65535 | C3 | USHORT | Upstream Pressure Address | NV | No | R/W |  | 1 | 65535 | 8356
| UpstrmPModbusSpcfr | 414273 | Upstream Pressure Modbus Specifier | 1 | 2 or 3 | C3 | USHORT | Upstream Pressure Modbus Specifier | NV | No | R/W |  | 2 | 3 | 3
| UpstrmTempDeviceID | 414274 | Upstream Temperature Device ID | 1 | -1, 1 to 247 | C3 | USHORT | Upstream Temperature Device ID | NV | No | R/W |  | -1 | 247 | 1
| UpstrmTempAd | 414275 | Upstream Temperature Address | 1 | 1 to 65535 | C3 | USHORT | Upstream Temperature Address | NV | No | R/W |  | 1 | 65535 | 8358
| UpstrmTempModbusSpcfr | 414276 | Upstream Temperature Modbus Specifier | 1 | 2 or 3 | C3 | USHORT | Upstream Temperature Modbus Specifier | NV | No | R/W |  | 2 | 3 | 3
| ThrtDiffPDeviceID | 414277 | Throat Differential Pressure Device ID | 1 | -1, 1 to 247 | C3 | USHORT | Throat Differential Pressure Device ID | NV | No | R/W |  | -1 | 247 | 1
| ThrtDiffPAd | 414278 | Throat Differential Pressure Address | 1 | 1 to 65535 | C3 | USHORT | Throat Differential Pressure Address | NV | No | R/W |  | 1 | 65535 | 8360
| ThrtDiffPModbusSpcfr | 414279 | Throat Differential Pressure Modbus Specifier | 1 | 2 or 3 | C3 | USHORT | Throat Differential Pressure Modbus Specifier | NV | No | R/W |  | 2 | 3 | 3
| RcvryDiffPDeviceID | 414280 | Recovery Differential Pressure Device ID | 1 | -1, 1 to 247 | C3 | USHORT | Recovery Differential Pressure Device ID | NV | No | R/W |  | -1 | 247 | 1
| RcvryDiffPAd | 414281 | Recovery Differential Pressure Address | 1 | 1 to 65535 | C3 | USHORT | Recovery Differential Pressure Address | NV | No | R/W |  | 1 | 65535 | 8362
| RcvryDiffPModbusSpcfr | 414282 | Recovery Differential Pressure Modbus Specifier | 1 | 2 or 3 | C3 | USHORT | Recovery Differential Pressure Modbus Specifier | NV | No | R/W |  | 2 | 3 | 3
|  | 414283 | Reserved | 718 |  | C3

## ISaGRAF_Error
Error Code | Error Description
-01 | Startup error.
-02 | Server communication exchange: Accept error.
-03 | Resource Restore error.
-04 | Kernel Retain: Init error.
-05 | Kernel Retain: Bad memory description.
-06 | Kernel Retain: CRC error.
-07 | Kernel Retain: Read error.
-08 | Kernel Retain: Write error.
-09 | Resource Data Allocation error.
-10 | Resource Start Report.
-11 | Resource Stop Report.
-12 | Standard function not implemented.
-13 | Standard function block instance init not implemented.
-14 | Standard function block instance exit not implemented.
-15 | Standard function block call not implemented.
-16 | Function not implemented.
-17 | Function block instance init required but not implemented.
-18 | Function block instance exit required but not implemented.
-19 | Function block call not implemented.
-20 | Function not implemented.
-21 | Kernel IOs: Init error.
-22 | Kernel IOs: Driver Init/Exit fct(s) not found.
-23 | Kernel IOs: Device Open/Close fct(s) not found.
-24 | Kernel IOs: Device Read fct not found.
-25 | Kernel IOs: Device Write fct not found.
-26 | Kernel IOs: Device Control fct not found.
-27 | Kernel IOs: Driver Init fct failure.
-28 | Kernel IOs: Device Open fct failure.
-29 | Kernel Binding: Driver not found.
-30 | Kernel Binding: Init error.
-31 | Kernel TIC: Unknown tic code.
-32 | Kernel TIC: Cast error.
-33 | Kernel TIC: Boundary check error.
-34 | Kernel TIC: SINT divided by zero.
-35 | Kernel TIC: DINT divided by zero.
-36 | Kernel TIC: REAL divided by zero.
-37 | Dynamic SFC behaviour: Behaviour processing error.
-38 | Dynamic SFC behaviour: Action Execution error.
-39 | Cycle Time Overflow.
-40 | Dynamic SFC behaviour: Initialisation error.
-41 | Kernel TIC: INT divided by zero.
-48 | Kernel TIC: LINT divided by zero.
-49 | Kernel TIC: USINT divided by zero.
-50 | Kernel TIC: UINT divided by zero.
-51 | Kernel TIC: UDINT divided by zero.
-52 | Kernel TIC: ULINT divided by zero.
-53 | Kernel TIC: LREAL divided by zero.

## TimeZone
Index | Offset | Time Zone Name | DST
1 | UTC-12:00 | International Date Line West | Not Applicable
2 | UTC-11:00 | Coordinated Universal Time-11 | Not Applicable
3 | UTC-10:00 | Aleutian Islands | Applicable
4 | UTC-10:00 | Hawaii | Not Applicable
5 | UTC-09:30 | Marquesas Islands | Not Applicable
6 | UTC-09:00 | Alaska | Applicable
7 | UTC-09:00 | Coordinated Universal Time-09 | Not Applicable
8 | UTC-08:00 | Baja California | Applicable
9 | UTC-08:00 | Coordinated Universal Time-08 | Not Applicable
10 | UTC-08:00 | Pacific Time (US & Canada) | Applicable
11 | UTC-07:00 | Arizona | Not Applicable
12 | UTC-07:00 | Chihuahua, La Paz, Mazatlan | Applicable
13 | UTC-07:00 | Mountain Time (US & Canada) | Applicable
14 | UTC-06:00 | Central America | Not Applicable
15 | UTC-06:00 | Central Time (US & Canada) | Applicable
16 | UTC-06:00 | Easter Island | Applicable
17 | UTC-06:00 | Guadalajara, Mexico City, Monterrey | Applicable
18 | UTC-06:00 | Saskatchewan | Not Applicable
19 | UTC-05:00 | Bogota, Lima, Quito, Rio Branco | Not Applicable
20 | UTC-05:00 | Chetumal | Not Applicable
21 | UTC-05:00 | Eastern Time (US & Canada) | Applicable
22 | UTC-05:00 | Haiti | Applicable
23 | UTC-05:00 | Havana | Applicable
24 | UTC-05:00 | Indiana (East) | Applicable
25 | UTC-05:00 | Turks and Caicos | Applicable
26 | UTC-04:00 | Asuncion | Applicable
27 | UTC-04:00 | Atlantic Time (Canada) | Applicable
28 | UTC-04:00 | Caracas | Not Applicable
29 | UTC-04:00 | Cuiaba | Applicable
30 | UTC-04:00 | Georgetown, La Paz, Manaus, San Juan | Not Applicable
31 | UTC-04:00 | Santiago | Applicable
32 | UTC-03:30 | Newfoundland | Applicable
33 | UTC-03:00 | Araguaina | Not Applicable
34 | UTC-03:00 | Brasilia | Applicable
35 | UTC-03:00 | Cayenne, Fortaleza | Not Applicable
36 | UTC-03:00 | City of Buenos Aires | Not Applicable
37 | UTC-03:00 | Greenland | Applicable
38 | UTC-03:00 | Montevideo | Not Applicable
39 | UTC-03:00 | Punta Arenas | Not Applicable
40 | UTC-03:00 | Saint Pierre and Miquelon | Applicable
41 | UTC-03:00 | Salvador | Not Applicable
42 | UTC-02:00 | Coordinated Universal Time-02 | Not Applicable
43 | UTC-01:00 | Azores | Applicable
44 | UTC-01:00 | Cabo Verde Is. | Not Applicable
45 | UTC | Coordinated Universal Time | Not Applicable
46 | UTC+00:00 | Casablanca | Applicable
47 | UTC+00:00 | Dublin, Edinburgh, Lisbon, London | Applicable
48 | UTC+00:00 | Monrovia, Reykjavik | Not Applicable
49 | UTC+01:00 | Amsterdam, Berlin, Bern, Rome, Stockholm, Vienna | Applicable
50 | UTC+01:00 | Belgrade, Bratislava, Budapest, Ljubljana, Prague | Applicable
51 | UTC+01:00 | Brussels, Copenhagen, Madrid, Paris | Applicable
52 | UTC+01:00 | Coordinated Universal Time+01 | Not Applicable
53 | UTC+01:00 | Sarajevo, Skopje, Warsaw, Zagreb | Applicable
54 | UTC+01:00 | West Central Africa | Not Applicable
55 | UTC+02:00 | Amman | Applicable
56 | UTC+02:00 | Athens, Bucharest | Applicable
57 | UTC+02:00 | Beirut | Applicable
58 | UTC+02:00 | Cairo | Not Applicable
59 | UTC+02:00 | Chisinau | Applicable
60 | UTC+02:00 | Damascus | Applicable
61 | UTC+02:00 | Gaza, Hebron | Applicable
62 | UTC+02:00 | Harare, Pretoria | Not Applicable
63 | UTC+02:00 | Helsinki, Kyiv, Riga, Sofia, Tallinn, Vilnius | Applicable
64 | UTC+02:00 | Jerusalem | Applicable
65 | UTC+02:00 | Kaliningrad | Not Applicable
66 | UTC+02:00 | Khartoum | Not Applicable
67 | UTC+02:00 | Tripoli | Not Applicable
68 | UTC+02:00 | Windhoek | Not Applicable
69 | UTC+03:00 | Baghdad | Not Applicable
70 | UTC+03:00 | Istanbul | Not Applicable
71 | UTC+03:00 | Kuwait, Riyadh | Not Applicable
72 | UTC+03:00 | Minsk | Not Applicable
73 | UTC+03:00 | Moscow, St. Petersburg, Volgograd | Not Applicable
74 | UTC+03:00 | Nairobi | Not Applicable
75 | UTC+03:30 | Tehran | Applicable
76 | UTC+04:00 | Abu Dhabi, Muscat | Not Applicable
77 | UTC+04:00 | Astrakhan, Ulyanovsk | Not Applicable
78 | UTC+04:00 | Baku | Not Applicable
79 | UTC+04:00 | Izhevsk, Samara | Not Applicable
80 | UTC+04:00 | Port Louis | Not Applicable
81 | UTC+04:00 | Saratov | Not Applicable
82 | UTC+04:00 | Tbilisi | Not Applicable
83 | UTC+04:00 | Yerevan | Not Applicable
84 | UTC+04:30 | Kabul | Not Applicable
85 | UTC+05:00 | Ashgabat, Tashkent | Not Applicable
86 | UTC+05:00 | Ekaterinburg | Not Applicable
87 | UTC+05:00 | Islamabad, Karachi | Not Applicable
88 | UTC+05:30 | Chennai, Kolkata, Mumbai, New Delhi | Not Applicable
89 | UTC+05:30 | Sri Jayawardenepura | Not Applicable
90 | UTC+05:45 | Kathmandu | Not Applicable
91 | UTC+06:00 | Astana | Not Applicable
92 | UTC+06:00 | Dhaka | Not Applicable
93 | UTC+06:00 | Omsk | Not Applicable
94 | UTC+06:30 | Yangon (Rangoon) | Not Applicable
95 | UTC+07:00 | Bangkok, Hanoi, Jakarta | Not Applicable
96 | UTC+07:00 | Barnaul, Gorno-Altaysk | Not Applicable
97 | UTC+07:00 | Hovd | Not Applicable
98 | UTC+07:00 | Krasnoyarsk | Not Applicable
99 | UTC+07:00 | Novosibirsk | Not Applicable
100 | UTC+07:00 | Tomsk | Not Applicable
101 | UTC+08:00 | Beijing, Chongqing, Hong Kong, Urumqi | Not Applicable
102 | UTC+08:00 | Irkutsk | Not Applicable
103 | UTC+08:00 | Kuala Lumpur, Singapore | Not Applicable
104 | UTC+08:00 | Perth | Not Applicable
105 | UTC+08:00 | Taipei | Not Applicable
106 | UTC+08:00 | Ulaanbaatar | Not Applicable
107 | UTC+09:00 | Pyongyang | Not Applicable
108 | UTC+08:45 | Eucla | Not Applicable
109 | UTC+09:00 | Chita | Not Applicable
110 | UTC+09:00 | Osaka, Sapporo, Tokyo | Not Applicable
111 | UTC+09:00 | Seoul | Not Applicable
112 | UTC+09:00 | Yakutsk | Not Applicable
113 | UTC+09:30 | Adelaide | Applicable
114 | UTC+09:30 | Darwin | Not Applicable
115 | UTC+10:00 | Brisbane | Not Applicable
116 | UTC+10:00 | Canberra, Melbourne, Sydney | Applicable
117 | UTC+10:00 | Guam, Port Moresby | Not Applicable
118 | UTC+10:00 | Hobart | Applicable
119 | UTC+10:00 | Vladivostok | Not Applicable
120 | UTC+10:30 | Lord Howe Island | Applicable
121 | UTC+11:00 | Bougainville Island | Not Applicable
122 | UTC+11:00 | Chokurdakh | Not Applicable
123 | UTC+11:00 | Magadan | Not Applicable
124 | UTC+11:00 | Norfolk Island | Not Applicable
125 | UTC+11:00 | Sakhalin | Not Applicable
126 | UTC+11:00 | Solomon Is., New Caledonia | Not Applicable
127 | UTC+12:00 | Anadyr, Petropavlovsk-Kamchatsky | Not Applicable
128 | UTC+12:00 | Auckland, Wellington | Applicable
129 | UTC+12:00 | Coordinated Universal Time+12 | Not Applicable
130 | UTC+12:00 | Fiji | Applicable
131 | UTC+12:45 | Chatham Islands | Applicable
132 | UTC+13:00 | Coordinated Universal Time+13 | Not Applicable
133 | UTC+13:00 | Nuku'alofa | Not Applicable
134 | UTC+13:00 | Samoa | Applicable
135 | UTC+14:00 | Kiritimati Island | Not Applicable

## Gas Flow Measurement Events
Event Log Description | Event Log Code | Enron Address (Event Log ID) | Change Bitmap
Meter Identifier1 changed | OP_EVENT_METER_IDENTIFIER_1 | 201 | 0x0201
Meter Identifier2 changed | OP_EVENT_METER_IDENTIFIER_2 | 202 | 0x0201
Date changed | OP_EVENT_DATE | 203 | 0x0201
Time changed | OP_EVENT_TIME | 204 | 0x0201
Contact hour changed | OP_EVENT_CONTRACT_HOUR | 205 | 0x0201
Atmospheric Pressure changed | OP_EVENT_ATMOSPHERIC_PRESSURE | 206 | 0x0201
Base pressure changed | OP_EVENT_PRESSURE_BASE [PB] | 207 | 0x0201
Base temperature changed | OP_EVENT_TEMPERATURE_BASE [TB] | 208 | 0x0201
Temperature mode changed | OP_EVENT_TEMP_MODE | 209 | 0x0201
Pressure mode changed | OP_EVENT_PRESS_MODE | 210 | 0x0201
Differential pressure mode changed | OP_EVENT_DIFF_PRESS_MODE | 211 | 0x0201
Flowing Density mode changed | OP_EVENT_DENSITY_MODE [RHOTP] | 212 | 0x0201
Compressibility mode changed | OP_EVENT_COMPRESSIBILITY_MODE [ZF] | 213 | 0x0201
Water Cut mode changed | OP_EVENT_WATERCUT_MODE | 214 | 0x0201
Pulse Count mode changed | OP_EVENT_PULSE_COUNT_MODE | 215 | 0x0201
RHOS mode changed | OP_RHOS_MODE | 216 | 0x0201
Temperature input AI channel changed | OP_EVENT_TEMP_AI_SELECTION | 217 | 0x0201
Pressure input AI channel changed | OP_EVENT_PRESS_AI_SELECTION | 218 | 0x0201
Diff. Pressure input AI channel changed | OP_EVENT_DIFF_PRESS_AI_SELECTION | 219 | 0x0201
Density input AI channel changed | OP_EVENT_DENSITY_AI_SELECTION | 220 | 0x0201
Water Cut inputAI channel changed | OP_EVENT_WATERCUT_AI_SELECTION | 221 | 0x0201
Pressure engineering unit changed | OP_EVENT_PRESS_ENG_UNITS | 222 | 0x0201
Diff. Pressure engineering unit changed | OP_EVENT_DIFF_PRESS_ENG_UNITS | 223 | 0x0201
Temperature engineering unit changed | OP_EVENT_TEMP_ENG_UNITS | 224 | 0x0201
Flow engineering unit changed | OP_EVENT_FLOW_ENG_UNITS | 225 | 0x0201
Flow Calculation equation changed | OP_EVENT_FLOW_CALC_EQUATION | 226 | 0x0201
Gas Component 1 (Methane) changed | OP_EVENT_GAS_COMPONENT_CH4 | 227 | 0x0201
Gas Component 2 (Nitrogen) changed | OP_EVENT_GAS_COMPONENT_N2 | 228 | 0x0201
Gas Component 3 (Carbon Di-oxide) changed | OP_EVENT_GAS_COMPONENT_CO2 | 229 | 0x0201
Gas Component 4 (Ethane) changed | OP_EVENT_GAS_COMPONENT_C2H6 | 230 | 0x0201
Gas Component 5 (Propane) changed | OP_EVENT_GAS_COMPONENT_C3H8 | 231 | 0x0201
Gas Component 6 (Water) changed | OP_EVENT_GAS_COMPONENT_H2O | 232 | 0x0201
Gas Component 7 (Hydrogen Sulfide) changed | OP_EVENT_GAS_COMPONENT_H2S | 233 | 0x0201
Gas Component 8 (Hydrogen) changed | OP_EVENT_GAS_COMPONENT_H2 | 234 | 0x0201
Gas Component 9 (Carbon Mono-oxide) changed | OP_EVENT_GAS_COMPONENT_CO | 235 | 0x0201
Gas Component 10 (Oxygen) changed | OP_EVENT_GAS_COMPONENT_O2 | 236 | 0x0201
Gas Component 11 (I-Butane) changed | OP_EVENT_GAS_COMPONENT_I_C4H10 | 237 | 0x0201
Gas Component 12 (N-Butane) changed | OP_EVENT_GAS_COMPONENT_N_C4H10 | 238 | 0x0201
Gas Component 13 (I-Pentane) changed | OP_EVENT_GAS_COMPONENT_I_C5H12 | 239 | 0x0201
Gas Component 14 (N-Pentane) changed | OP_EVENT_GAS_COMPONENT_N_C5H12 | 240 | 0x0201
Gas Component 15 (Hexane) changed | OP_EVENT_GAS_COMPONENT_C6H14 | 241 | 0x0201
Gas Component 16 (Heptane) changed | OP_EVENT_GAS_COMPONENT_C7H16 | 242 | 0x0201
Gas Component 17 (Octane) changed | OP_EVENT_GAS_COMPONENT_C8H18 | 243 | 0x0201
Gas Component 18 (Nonane) changed | OP_EVENT_GAS_COMPONENT_C9H2O | 244 | 0x0201
Gas Component 19 (Decane) changed | OP_EVENT_GAS_COMPONENT_C10H22 | 245 | 0x0201
Gas Component 20 (Helium) changed | OP_EVENT_GAS_COMPONENT_HE | 246 | 0x0201
Gas Component 21 (Argon) changed | OP_EVENT_GAS_COMPONENT_AR | 247 | 0x0201
Heating number changed | OP_EVENT_HEATING_NUMBER [HV] | 248 | 0x0201
Meter tube reference inside diameter changed | OP_EVENT_METER_TUBE_REF_INSIDE [DM] | 249 | 0x0201
Orifice Plate Ref bore size changed | OP_EVENT_ORIFICE_PLATE_REF_BORE_SIZE [DO] | 250 | 0x0201
Static pressure Tap Location changed | OP_EVENT_STATIC_PRESS_TAP_LOCATION [NPLOC] | 251 | 0x0201
Orifice plate material or expansion factor changed | OP_EVENT_ORIFICE_PLATE_MATERIAL [MATORF] | 252 | 0x0201
Orifice tube material changed | OP_EVENT_METER_TUBE_MATERIAL [ MATPIPE] | 253 | 0x0201
Viscosity changed | OP_EVENT_VISCOSITY [VISC] | 254 | 0x0201
Orifice Diameter Measurement Temperature value changed | OP_EVENT_ORIFICE DIAMETER MEASUREMENT TEMPERATURE [TORF] | 255 | 0x0201
Pipe Diameter Measurement Temperature value changed | OP_EVENT_PIPE DIAMETER MEASUREMENT TEMPERATURE [TPIPE] | 256 | 0x0201
Isentropic Exponent value changed | OP_EVENT_ISENTROPIC EXPONENT [KFAC] | 257 | 0x0201
Calibration Factor value changed | OP_EVENT_CALIBRATION FACTOR [FACTR] | 258 | 0x0201
Compressibility Factor of Air at TS & PS [ZAIRS] value changed | OP_EVENT_COMPRESSIBILITY FACTOR OF AIR AT TS & PS [ZAIRS] | 259 | 0x0201
Base Compressibility Factor of Air [ZAIRB] value changed | OP_EVENT_BASE COMPRESSIBILITY FACTOR OF AIR [ZAIRB] | 260 | 0x0201
Low Diff cutoff parameter changed | OP_EVENT_FLOW_DIFF_CUTOFF | 261 | 0x0201
Meter factor changed | OP_EVENT_METER_FACTOR [MF] | 262 | 0x0201
K factor changed | OP_EVENT_K_FACTOR [KF] | 263 | 0x0201
Linear factor 1 changed | OP_EVENT_LINEAR_FACTOR_1 | 264 | 0x0201
Linear factor 2 changed | OP_EVENT_LINEAR_FACTOR_2 | 265 | 0x0201
Linear factor 3 changed | OP_EVENT_LINEAR_FACTOR_3 | 266 | 0x0201
Linear factor 4 changed | OP_EVENT_LINEAR_FACTOR_4 | 267 | 0x0201
Linear factor 5 changed | OP_EVENT_LINEAR_FACTOR_5 | 268 | 0x0201
Linear factor 6 changed | OP_EVENT_LINEAR_FACTOR_6 | 269 | 0x0201
Linear factor 7 changed | OP_EVENT_LINEAR_FACTOR_7 | 270 | 0x0201
Linear factor 8 changed | OP_EVENT_LINEAR_FACTOR_8 | 271 | 0x0201
Linear factor 9 changed | OP_EVENT_LINEAR_FACTOR_9 | 272 | 0x0201
Linear factor 10 changed | OP_EVENT_LINEAR_FACTOR_10 | 273 | 0x0201
Linear factor 11 changed | OP_EVENT_LINEAR_FACTOR_11 | 274 | 0x0201
Linear factor 12 changed | OP_EVENT_LINEAR_FACTOR_12 | 275 | 0x0201
Linear factor threshold 1 changed | OP_EVENT_LINEAR_FACTOR_THRESHOLD_1 | 276 | 0x0201
Linear factor threshold 2 changed | OP_EVENT_LINEAR_FACTOR_THRESHOLD_2 | 277 | 0x0201
Linear factor threshold 3 changed | OP_EVENT_LINEAR_FACTOR_THRESHOLD_3 | 278 | 0x0201
Linear factor threshold 4 changed | OP_EVENT_LINEAR_FACTOR_THRESHOLD_4 | 279 | 0x0201
Linear factor threshold 5 changed | OP_EVENT_LINEAR_FACTOR_THRESHOLD_5 | 280 | 0x0201
Linear factor threshold 6 changed | OP_EVENT_LINEAR_FACTOR_THRESHOLD_6 | 281 | 0x0201
Linear factor threshold 7 changed | OP_EVENT_LINEAR_FACTOR_THRESHOLD_7 | 282 | 0x0201
Linear factor threshold 8 changed | OP_EVENT_LINEAR_FACTOR_THRESHOLD_8 | 283 | 0x0201
Linear factor threshold 9 changed | OP_EVENT_LINEAR_FACTOR_THRESHOLD_9 | 284 | 0x0201
Linear factor threshold 10 changed | OP_EVENT_LINEAR_FACTOR_THRESHOLD_10 | 285 | 0x0201
Linear factor threshold 11 changed | OP_EVENT_LINEAR_FACTOR_THRESHOLD_11 | 286 | 0x0201
Linear factor threshold 12 changed | OP_EVENT_LINEAR_FACTOR_THRESHOLD_12 | 287 | 0x0201
Low Frequency cutoff parameter changed | OP_EVENT_LOW_FREQ_CUTTOFF | 288 | 0x0201
ISaGRAF Flow Application Start | OP_EVENT_ISAGRAF_FLOW_APP_START | 289 | 0x0201
System in global maintenance mode | OP_EVENT_GLOBAL_MAINTENANCE_MODE | 290 | 0x0201
Static Pressure Low Alarm Enable | OP_EVENT_STATIC_PRESSURE_LOW_ALARM_ENABLE | 291 | 0x0201
Static Pressure High Alarm Enable | OP_EVENT_STATIC_PRESSURE_HIGH_ALARM_ENABLE | 292 | 0x0201
Temperature Low Alarm Enable | OP_EVENT_TEMPERATURE_LOW_ALARM_ENABLE | 293 | 0x0201
Temperature High Alarm Enable | OP_EVENT_TEMPERATURE_HIGH_ALARM_ENABLE | 294 | 0x0201
Differential Pressure Low Alarm Enable | OP_EVENT_DIFF_PRESSURE_LOW_ALARM_ENABLE | 295 | 0x0201
Differential Pressure High Alarm Enable | OP_EVENT_DIFF_PRESSURE_HIGH_ALARM_ENABLE | 296 | 0x0201
Density Low Alarm Enable | OP_EVENT_DENSITY_LOW_ALARM_ENABLE | 297 | 0x0201
Density High Alarm Enable | OP_EVENT_DENSITY_HIGH_ALARM_ENABLE | 298 | 0x0201
Water Cut Low Alarm Enable | OP_EVENT_WATER_CUT_LOW_ALARM_ENABLE | 299 | 0x0201
Water Cut High Alarm Enable | OP_EVENT_WATER_CUT_HIGH_ALARM_ENABLE | 300 | 0x0201
Flow Rate Low Alarm Enable | OP_EVENT_FLOW_RATE_LOW_ALARM_ENABLE | 301 | 0x0201
Flow Rate High Alarm Enable | OP_EVENT_FLOW_RATE_HIGH_ALARM_ENABLE | 302 | 0x0201
Static Pressure Low Setpoint changed | OP_EVENT_STATIC_PRESSURE_LOW_SP_CHANGED | 303 | 0x0201
Static Pressure High Setpoint changed | OP_EVENT_STATIC_PRESSURE_HIGH_SP_CHANGED | 304 | 0x0201
Temperature Low Setpoint changed | OP_EVENT_TEMPERATURE_LOW_SP_CHANGED | 305 | 0x0201
Temperature High Setpoint changed | OP_EVENT_TEMPERATURE_HIGH_SP_CHANGED | 306 | 0x0201
Differential Pressure Low Setpoint changed | OP_EVENT_DIFF_PRESSURE_LOW_SP_CHANGED | 307 | 0x0201
Differential Pressure High Setpoint changed | OP_EVENT_DIFF_PRESSURE_HIGH_SP_CHANGED | 308 | 0x0201
Density Low Setpoint changed | OP_EVENT_DENSITY_LOW_SP_CHANGED | 309 | 0x0201
Density High Setpoint changed | OP_EVENT_DENSITY_HIGH_SP_CHANGED | 310 | 0x0201
Water Cut Low Setpoint changed | OP_EVENT_WATER_CUT_LOW_SP_CHANGED | 311 | 0x0201
Water Cut High Setpoint changed | OP_EVENT_WATER_CUT_HIGH_SP_CHANGED | 312 | 0x0201
Flow Rate Low Setpoint changed | OP_EVENT_FLOW_RATE_LOW_SP_CHANGED | 313 | 0x0201
Flow Rate High Setpoint changed | OP_EVENT_FLOW_RATE_HIGH_SP_CHANGED | 314 | 0x0201
Static Pressure Deadband changed | OP_EVENT_STATIC_PRESSURE_DEADBAND_CHANGED | 315 | 0x0201
Temperature Deadband changed | OP_EVENT_TEMPERATURE_DEADBAND_CHANGED | 316 | 0x0201
Differential Pressure Deadband changed | OP_EVENT_DIFF_PRESSURE_DEADBAND_CHANGED | 317 | 0x0201
Density Deadband changed | OP_EVENT_DENSITY_DEADBAND_CHANGED | 318 | 0x0201
Water Cut Deadband changed | OP_EVENT_WATER_CUT_DEADBAND_CHANGED | 319 | 0x0201
Flow Rate Deadband changed | OP_EVENT_FLOW_RATE_DEADBAND_CHANGED | 320 | 0x0201
DO Engineering Unit changed | OP_EVENT_DO_ENG_UNITS | 321 | 0x0201
DM Engineering Unit changed | OP_EVENT_DM_ENG_UNITS | 322 | 0x0201
Density Engineering Unit changed | OP_EVENT_DENSITY_ENG_UNITS | 323 | 0x0201
Reset Historical Reports | OP_EVENT_RESET_HISTORICAL_REPORTS | 324 | 0x0201
Reserved |  | 325 - 400
Temperature above High Limit. When Temperature is read from AI channel OR Remote I/O then high/low limit is decided by the Alarm Low Set Point for Local/Remote TF and Alarm High Set Point for Local/Remote HR registers. | AL_EVENT_TEMPERATURE | 401 | 0x9000 = High Alarm 0x8800 = Low Alarm 0x0000 = In Range Alarm
Pressure above High Limit. Pressure high/low limits same as above for temperature | AL_EVENT_PRESSURE | 402 | 0x9000 = High Alarm 0x8800 = Low Alarm 0x0000 = In Range Alarm
Diff. Pressure above High Limit. Diff. Pressure high/low limits same as above for temperature | AL_EVENT_DIFFERENTIAL PRESSURE | 403 | 0x9000 = High Alarm 0x8800 = Low Alarm 0x0000 = In Range Alarm
Density above High Limit. Density high/low limits same as above for temperature | AL_EVENT_DENSITY | 404 | 0x9000 = High Alarm 0x8800 = Low Alarm 0x0000 = In Range Alarm
Flow rate above High Limit | AL_EVENT_FLOW RATE | 405 | 0x9000 = High Alarm 0x8800 = Low Alarm 0x0000 = In Range Alarm
Flow is below flow cutoff Limit | AL_EVENT_FLOW BELOW CUTOFF | 406 | 0x8800 = Low Alarm 0x0000 = In Range Alarm
Water Cut above High Limit | AL_EVENT_WATER CUT | 407 | 0x9000 = High Alarm 0x8800 = Low Alarm 0x0000 = In Range Alarm
Reserved |  | 408 - 500

## WMP Rev History
iXC2-Core WMP Modbus Register Mapping
Document History:
Doc Version | Date | Description
1.01 | 2015-03-18 | 01. Initial Draft
1.02 | 2016-11-30 | 01. Modified the Description and Tag Name of CS 201 - 300, Reset Message Count
1.03 | 2017-04-11 | 01. Removed the Default value from the Range Column

## WMP-CS
CP | Tag Name | MODBUS CS | Description | No of Registers | Range | Comm Type | Data type | Remark | Storage | On Demand | Access | UOM | Data Min | Data Max | Default
|  | 1 | Reserved | 100
| N1.SendMode | 101 | If bit is ON, it sets Bit 7 in the mail box byte (Byte 5) of message header for Transmitter 1 equal to FirstiTransID. Transmitter 1 will send register message when it gets the message from Gateway. Registers 101 will be reset to zero once action is taken. If FirstiTransID is 100 then transmitter with ID 100 will be stored here. | 1 | 0 or 1 | C3 | Bit | - | NV | No | R/W | - | - | - | 0
| N2.SendMode | 102 | Same for Transmitter 2. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 1 | 0 or 1 | C3 | Bit | - | NV | No | R/W | - | - | - | 0
| N3.SendMode,N100.SendMode | 103 | Same for Transmitter 3 to 100 | 98 | 0 or 1 | C3 | Bit | - | NV | No | R/W | - | - | - | 0
| N1.ResetMsgCnt | 201 | If bit is ON, it sets Bit 8 of the mailbox byte in WMP message header for Transmitter 1 equal to FirstiTransID.All the message counts like No of message received,sent will be reset to 0. Registers 201 will be reset to zero once action is taken.If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 1 | - | C3 | Bit | - | NV | No | R/W | - | - | - | 0
| N2.ResetMsgCnt | 202 | Same for Transmitter 2. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 1 | - | C3 | Bit | - | NV | No | R/W | - | - | - | 0
| N3.ResetMsgCnt, N100.ResetMsgCnt | 203 | Same for Transmitter 3 to 100 | 98 | - | C3 | Bit | - | NV | No | R/W | - | - | - | 0
|  | 301 | Reserved | 200 |  |  | Bit
| N1.ReadMode | 501 | Node 1 equal to FirstiTransID read mode (0-local, 1-remote). A value of 0 will cause the Gateway to respond to any MODBUS Master read request by sending back the last known value for transmitter node 1. On the other hand a value of 1 will cause the Gateway to route this request to the Transmitter and then send back the response received from the node. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 1 | 0 or 1 | C3 | Bit | - | NV | No | R/W | - | - | - | 0
| N2.ReadMode | 502 | Same for Transmitter 2. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 1 | 0 or 1 | C3 | Bit | - | NV | No | R/W | - | - | - | 0
| N3.ReadMode,N100.ReadMode | 503 | Same for Transmitter 3 to 100 | 98 | 0 or 1 | C3 | Bit | - | NV | No | R/W | - | - | - | 0
|  | 601 | Reserved | 3 |  |  | Bit
| AllNCntnsMode | 604 | A value of 1 will set all Transmitters running in continuous mode in remote read node. | 1 | 0 or 1 | C3 | Bit | - | NV | No | R/W | - | - | - | 0
|  | 605 | Reserved | 9395 |  |  | Bit

## WMP-IS
CP | Tag Name | MODBUS IS | Description | No of Registers | Default Value/ Range | Comm Type | Data type | Remarks | Storage | On Demand | Access | UOM | Data Min | Data Max | Default
|  | 10001 | Reserved | 1000 |  |  | Bit
| N1.Sts_DICh1 | 11001 | DI status for Channel 1 for Transmitter 1 equal to FirstiTransID. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 1 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N1.Sts_DICh2 | 11002 | DI status for Channel 2 for Transmitter 1 equal to FirstiTransID. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 1 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N1.Sts_DICh3 | 11003 | DI status for Channel 3 for Transmitter 1 equal to FirstiTransID. | 1 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N1.Sts_DICh4 | 11004 | DI status for Channel 4 for Transmitter 1 equal to FirstiTransID. | 1 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N1.Sts_DICh5, N1.Sts_DICh8 | 11005 | DI status for Channel 5 to 8 for Transmitter 1 equal to FirstiTransID. | 4 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N2.Sts_DICh1, N2.Sts_DICh8 | 11009 | DI status for Transmitter 2. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 8 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N3.Sts, N100.Sts | 11017 | DI status for for Transmitter 3 to 100. | 784 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
|  | 11801 | Reserved | 300
| N1.Sts_Alm | 12101 | Alarm Status for Transmitter 1 equal to FirstiTransID when message is not received for specified interval. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 1 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N2.Sts_Alm | 12102 | Alarm Status for Transmitter 2. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 1 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N3.Sts_Alm, N100.Sts_Alm | 12103 | Alarm Status for Transmitter 3 to 100. | 98 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
|  | 12201 | Reserved | 100
| N1.SleepWakeMd | 12301 | This value is one if Transmitter 1 equal to FirstiTransID is working in sleep and wake up mode. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 1 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N2.SleepWakeMd | 12302 | Same for Transmitter 2 | 1 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N3.SleepWakeMd, N100.SleepWakeMd | 12303 | Transmitter mode for Node 3 to 100. | 98 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N1.SerPrtclTyp | 12401 | Type of Serial Protocol supported by Transmitter 1 equal to FirstiTransID. For ASCII protocol its value is zero (0) and for RTU protocol its value is one (1).If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 1 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N2.SerPrtclTyp, N100.SerPrtclTyp | 12402 | Type of Serial Protocol supported by Transmitter 2 to 100. | 99 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N1.ActvTrnsmtr | 12501 | Active Transmitter Nodes (0-Inactive, 1-Active)for Transmitter 1 equal to FirstiTransID. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 1 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N2.ActvTrnsmtr | 12502 | Active Transmitter Nodes for Node 2 .If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 1 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N3.ActvTrnsmtr, N100.ActvTrnsmtr | 12503 | Active Transmitter Nodes for Transmitter 3 to 100. | 98 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N1.ActvUnRegd | 12601 | Active Unregistered Nodes (1-Unregistered Active node) for Transmitter 1 equal to FirstiTransID. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 1 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
| N2.ActvUnRegd, N100.ActvUnRegd | 12602 | Active Unregistered Nodes for Transmitter 2 to 100. | 99 | 0 or 1 | I3 | Bit | - | NV | No | R | - | - | - | 0
|  | 12701 | Reserved | 7300

## WMP-IR
CP | Tag Name | MODBUS IR | Description | No of Registers | Range | Comm Type | Data type | Remark | Storage | On Demand | Access | UOM | Data Min | Data Max | Default
| WMPMBSlvID | 30001 | WMP MODBUS Salve ID | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
|  | 30002 | Reserved | 2
| FWVerNum | 30004 | Firmware version number | 2 | - | I3 | FLOAT | - | NV | No | R | - | - | - | -
|  | 30006 | Reserved | 12
| NextAvbleID | 30018 | Next Available ID | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| FirstiTransID | 30019 | First iTrans ID | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
|  | 30020 | Reserved | 31
| N1.SerNum | 30051 | Serial Number of Transmitter 1 equal to FirstiTransID registered with Gateway. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 2 | - | I3 | LONG | - | NV | No | R | - | - | - | -
| N2.SerNum | 30053 | Serial Number for Transmitter 2. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 2 | - | I3 | LONG | - | NV | No | R | - | - | - | -
| N3.SerNum, N100.SerNum | 30055 | Same for Transmitter 3 to 100. | 196 | - | I3 | LONG | - | NV | No | R | - | - | - | -
|  | 30251 | Reserved | 300
| N1.RawCh1 | 30551 | Raw data for Channel 1 for Transmitter 1 equal to FirstiTransID registered with Gateway. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| N1.RawCh2 | 30552 | Raw data for Channel 2 for Transmitter 1 equal to FirstiTransID | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| N1.RawCh3 | 30553 | Raw data for Channel 3 for Transmitter 1 equal to FirstiTransID | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| N1.RawCh4 | 30554 | Raw data for Channel 4 for Transmitter 1 equal to FirstiTransID | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| N1.RawCh5, N1.RawCh10 | 30555 | Raw data for Channel 5 - 10 for Transmitter 1 equal to FirstiTransID | 6 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| N2.RawCh1, N2.RawCh10 | 30561 | Raw data for all channels for Transmitter 2. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 10 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| N3.RawCH, N100.RawCH | 30571 | Raw data for all channels for Transmitter 3 to 100. | 980 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| N1.EUCh1 | 31551 | EU data for Channel 1 for Transmitter 1 equal to FirstiTransID registered with Gateway. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 2 | - | I3 | FLOAT | - | NV | No | R | - | - | - | -
| N1.EUCh2 | 31553 | EU data for Channel 2 for Transmitter 1 equal to FirstiTransID. | 2 | - | I3 | FLOAT | - | NV | No | R | - | - | - | -
| N1.EUCh3 | 31555 | EU data for Channel 3 for Transmitter 1 equal to FirstiTransID. | 2 | - | I3 | FLOAT | - | NV | No | R | - | - | - | -
| N1.EUCh4 | 31557 | EU data for Channel 4 for Transmitter 1 equal to FirstiTransID. | 2 | - | I3 | FLOAT | - | NV | No | R | - | - | - | -
| N1.EUCh5, N1.EUCh10 | 31559 | EU data for Channel 5 - 10 for Transmitter 1 equal to FirstiTransID. | 12 | - | I3 | FLOAT | - | NV | No | R | - | - | - | -
| N2.EUCh1, N2.EUCh10 | 31571 | EU data for all channels for Transmitter 2. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 20 | - | I3 | FLOAT | - | NV | No | R | - | - | - | -
| N3.EUCh, N100.EUCh | 31591 | EU data for all channels for Transmitter 3 to 100. | 1960 | - | I3 | FLOAT | - | NV | No | R | - | - | - | -
| N1.RadioSigStrgth | 33551 | Node 1 equal to FirstiTransID Radio Signal Strength. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| N2.RadioSigStrgth | 33552 | Radio Signal Strength for Node 2. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| N3.RadioSigStrgth, N100.RadioSigStrgth | 33553 | Same for Transmitter 3 to 100. | 98 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| N1.RespsTm | 33651 | Response time in milliseconds for Transmitter 1 equal to FirstiTransID. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 1 | - | I3 | USHORT | - | NV | No | R | mSec | - | - | -
| N2.RespsTm | 33652 | Response time in milliseconds Node 2. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 1 | - | I3 | USHORT | - | NV | No | R | mSec | - | - | -
| N3.RespsTm, N100.RespsTm | 33653 | Same for Transmitter 3 to 100. | 98 | - | I3 | USHORT | - | NV | No | R | mSec | - | - | -
|  | 33751 | Reserved | 250
| N1.TmLastWMPMsg | 34001 | Time of Last WMP Message in seconds since 1970 for Transmitter 1 equal to FirstiTransID. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 2 | - | I3 | LONG | - | NV | No | R | Sec | - | - | -
| N2.TmLastWMPMsg | 34003 | Time of Last WMP Message in seconds since 1970 for Transmitter 2.If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 2 | - | I3 | LONG | - | NV | No | R | Sec | - | - | -
| N3.TmLastWMPMsg, N100.TmLastWMPMsg | 34005 | Same for Transmitter 3 to 100. | 196 | - | I3 | LONG | - | NV | No | R | Sec | - | - | -
| N1.TmSinceLastWMPMsg | 34201 | Time in seconds Since Last WMP Message for Transmitter 1 equal to FirstiTransID. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 2 | - | I1 | LONG | - | NV | No | R | Sec | - | - | -
| N2.TmSinceLastWMPMsg, N10.TmSinceLastWMPMsg | 34203 | Time in seconds Since Last WMP Message for Transmitter 2 to 10. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 18 | - | I1 | LONG | - | NV | No | R | Sec | - | - | -
| N11.TmSinceLastWMPMsg, N100.TmSinceLastWMPMsg | 34221 | Same for Transmitter 11 to 100. | 180 | - | I3 | LONG | - | NV | No | R | Sec | - | - | -
| N1.TmNextLastWMPMsg | 34401 | Time till next WMP message for Transmitter 1 equal to FirstiTransID. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 2 | - | I3 | LONG | - | NV | No | R | Sec | - | - | -
| N2.TmNextLastWMPMsg, N6.TmNextLastWMPMsg | 34403 | Time till next WMP message for Transmitter 2 to 6. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 10 | - | I3 | LONG | - | NV | No | R | Sec | - | - | -
| N7.TmNextLastWMPMsg, N100.TmNextLastWMPMsg | 34413 | Same for Transmitter 7 to 100. | 188 | - | I3 | LONG | - | NV | No | R | Sec | - | - | -
| N1.NumWMPMsgRcvd | 34601 | Number of WMP Messages Received from Transmitter 1 equal to FirstiTransID. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 2 | - | I3 | LONG | - | NV | No | R | - | - | - | -
| N2.NumWMPMsgRcvd, N6.NumWMPMsgRcvd | 34603 | Number of WMP Messages Received from Transmitter 2 to 6. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 10 | - | I3 | LONG | - | NV | No | R | - | - | - | -
| N7.NumWMPMsgRcvd, N100.NumWMPMsgRcvd | 34613 | Same for Transmitter 7 to 100. | 188 | - | I3 | LONG | - | NV | No | R | - | - | - | -
| N1.NumWMPMsgSent | 34801 | Number of WMP message sent from Gateway to the registered Transmitter 1 equal to FirstiTransID. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. | 2 | - | I3 | LONG | - | NV | No | R | - | - | - | -
| N2.NumWMPMsgSent, N6.NumWMPMsgSent | 34803 | Number of WMP message sent from Gateway to the registered Transmitter 2 to 6. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 10 | - | I3 | LONG | - | NV | No | R | - | - | - | -
| N7.NumWMPMsgSent, N100.NumWMPMsgSent | 34813 | Same for Transmitter 7 to 100. | 188 | - | I3 | LONG | - | NV | No | R | - | - | - | -
| N1.TrnsmtrCommEff | 35001 | Transmitter Communication Efficiency of number of messages sent by Gateway for Transmitter 1 equal to FirstiTransID. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. (Transmitter No of message received IR 27-28 of transmitter / Transmitter no of message sent IR 25-26) | 2 | - | I3 | FLOAT | - | NV | No | R | - | - | - | -
| N2.TrnsmtrCommEff, N6.TrnsmtrCommEff | 35003 | Transmitter Communication Efficiency of number of messages sent by the Gateway for Transmitter 2 to 6. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 10 | - | I3 | FLOAT | - | NV | No | R | - | - | - | -
| N7.TrnsmtrCommEff, N100.TrnsmtrCommEff | 35013 | Same for Transmitter 7 to 100. | 188 | - | I3 | FLOAT | - | NV | No | R | - | - | - | -
| N1.GtWyCommEff | 35201 | Gateway communication Efficiency for No of messages sent by the Transmitter for Transmitter 1 equal to FirstiTransID. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here.(Gateway no of message received IR 4601-4800 series register for the Transmitter / Transmitter # msg sent IR 25-26) | 2 | - | I3 | FLOAT | - | NV | No | R | - | - | - | -
| N2.GtWyCommEff, N6.GtWyCommEff | 35203 | Gateway communication Efficiency for No of messages sent by the Transmitter for Transmitter 2. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 10 | - | I3 | FLOAT | - | NV | No | R | - | - | - | -
| N7.GtWyCommEff, N100.GtWyCommEff | 35213 | Same for Transmitter 7 to 100. | 188 | - | I3 | FLOAT | - | NV | No | R | - | - | - | -
|  | 35401 | Reserved | 500 | - |  |  | - |  |  |  |  | - | - | -
| N1.FadeMarginRadioSig | 35901 | Fade Margin of the radio signal for Transmitter 1 equal to FirstiTransID when the Gateway is working in API mode. Fade Margin = (-1*RSSI for that Transmitter) - (Radio Receiver Sensitivity) . RSSI of a node is stored in the register range IR 3551 – 3650 depending upon the Transmitter ID. Radio Receiver Sensitivity is user defined and can be modified in the register HR 177. | 1 | - | I3 | SHORT | - | NV | No | R | - | - | - | -
| N2.FadeMarginRadioSig | 35902 | Fade Margin of the radio signal for Transmitter 2. If FirstiTransID is 100 then Transmitter with ID 101 will be stored here. | 1 | - | I3 | SHORT | - | NV | No | R | - | - | - | -
| N3.FadeMarginRadioSig, N100.FadeMarginRadioSig | 35903 | Same for Transmitter 3 to 100. | 98 | - | I3 | SHORT | - | NV | No | R | - | - | - | -
|  | 36001 | Reserved | 200
| N1.TransTyp | 36201 | Transmitter type for Transmitter 1 equal to FirstiTransID. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| N2.TransTyp, N100.TransTyp | 36202 | Same for Transmitter 2 to 100. | 99 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
|  | 36301 | Reserved | 31 |  | I3 | USHORT |  |  |  | R
| NumOORMsg | 36332 | No Of Out of range Transmitters (If a Transmitter ID is not in the range of First iTrans ID and First iTrans ID+ 99 then it is a out of range node). It should not be more than 10. | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| NIDFirstOORN | 36333 | Transmitter ID of the First Out of Range Node | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| SerNumFirstOORN | 36334 | Serial Number of the First Out of range Node | 2 | - | I3 | LONG | - | NV | No | R | - | - | - | -
| NIDSecondOORN | 36336 | Transmitter ID of the Second Out of Range Node | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| SerNumSecondOORN | 36337 | Serial Number of the Second Out of range Node | 2 | - | I3 | LONG | - | NV | No | R | - | - | - | -
| NIDThirdOORN, SerNumThirdOORN - NIDTenthOORN, SerNumTenthOORN | 36339 | Same as 6333-6335 for the 3rd to 10th Transmitter. | 24 | - | I3 |  | - | NV | No | R | - | - | - | -
| NumRjtdSerNum | 36363 | No of Rejected serial number (if serial number filtering feature is ON and if a serial number is not present in the WMP Configuration file ). It should not be more than 10 | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| FirstRjtdSerNum | 36364 | First Rejected serial Number | 2 | - |  | LONG | - | NV | No | R | - | - | - | -
| SecondRjtdSerNum, TenthRjtdSerNum | 36366 | 2nd to 10th Rejected serial number | 18 | - | I3 |  | - | NV | No | R | - | - | - | -
|  | 36384 | Reserved | 17
| Trans1ActvAlmStsAICh1 | 36401 | Active Alarms status for AI channel 1 for Transmitter 1 equal to FirstiTransID. If FirstiTransID is 100 then Transmitter with ID 100 will be stored here. 0 - No Alarm 1 - Low Alarm 2 - High Alarm 3-Percentage Change Alarm 4- Low with Percentage Change Alarm 5 - High With Percentage Change Alarm | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| Trans1ActvAlmStsAICh2 | 36402 | Active Alarms status for AI channel 2 for Transmitter 1 equal to FirstiTransID. | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| Trans1ActvAlmStsAICh3, Trans1ActvAlmStsAICh10 | 36403 | Active Alarms status for AI channel 3 -10 for Transmitter 1 equal to FirstiTransID. | 8 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| Trans2ActvAlmStsAICh1 | 36411 | Active Alarms status for AI Channel 1 Transmitter 2. If FirstiTransID is 100 then Node with ID 101 will be stored here. | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| Trans2ActvAlmStsAICh2 | 36412 | Active Alarms status for AI Channel 2 for Transmitter 2. If FirstiTransID is 100 then Node with ID 101 will be stored here. | 1 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| Trans2ActvAlmStsAICh3, Trans2ActvAlmStsAICh10 | 36413 | Active Alarms status for AI channel 3 -10 for Transmitter 2. | 8 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
| Trans3ActvAlmStsAICh, Trans100ActvAlmStsAICh | 36421 | Same for Transmitter 3 to 100. | 980 | - | I3 | USHORT | - | NV | No | R | - | - | - | -
|  | 37401 | Reserved | 2569

## WMP-HR
CP | Tag Name | MODBUS HR | Description | No of Registers | Range | Comm Type | Data type | Remark | Storage | On Demand | Access | UOM | Data Min | Data Max | Default
|  | 40001 | Reserved | 110
| TransSerNum | 40111 | Serial Number of the Transmitter to change ID | 2 | - | C3 | LONG | - | NV | No | R/W | - | - | - | 0
| TransCID | 40113 | Current ID of the Transmitter to change | 1 | - | C3 | USHORT | - | NV | No | R/W | - | - | - | 0
| TransNewID | 40114 | New ID of the Transmitter to change to | 1 | - | C3 | USHORT | - | NV | No | R/W | - | - | - | 0
| ChngID | 40115 | Change ID. Writing one will send ChangeID WMP command to transmitter. Registers 115 will be reset to zero once action is taken. | 1 | - | C3 | USHORT | - | NV | No | R/W | - | - | - | 0
| NumRetryGtWy | 40116 | Number of retry for Gateway in case no response received either Acknowledge or Error. Maximum retry will be 10. | 1 | - | C3 | USHORT | - | NV | No | R/W | - | - | - | 0
| AckTmoutGtWy | 40117 | Acknowledge Timeout in seconds for Gateway. | 1 | - | C3 | USHORT | - | NV | No | R/W | - | - | - | 0
|  | 40118 | Reserved | 1 |  |  | USHORT
| RadioAPIMd | 40119 | Radio API Mode (0-Transparent, 100-API) | 1 | - | C3 | USHORT | - | NV | No | RW | - | - | - | 0
|  | 40120 | Reserved | 44
| MsgBurst | 40164 | Message Burst Number (1, 2, 3, 4, or 5). | 1 | 1 to 5 | C3 | USHORT | - | NV | No | RW | - | 1 | 5 | 1
| NumMsgResetTm | 40165 | Number Of Message Reset time in minutes. -1 - Disable, 0 - Reset At Midnight, Range 1-1440. Default value is 0. | 1 | - | C3 | USHORT | - | NV | No | RW | Min |  |  | 0
|  | 40166 | Reserved | 4
| ResetGtWyNRcvdWMPMsg | 40170 | Reset the Gateway Nodes Received WMP message count. Writing a value of 100 will reset node 100-message count, 101 will reset node 101 message counts, etc. A value of 1000 will reset all the node received WMP message counts. | 1 | - | C3 | USHORT | - | NV | No | RW | - | - | - | 0
| ResetGtWyNAlm | 40171 | Reset the Gateway Node Alarm Flags Input Registers 6401 to 7400. It will reset the Min/Max and Percentage change alarm flags for the Transmitter also. Writing a value of 100 will reset alamr status for Transmitter ID 100, 101 will reset for ID 101 etc. | 1 | - | C3 | USHORT | - | NV | No | RW | - | - | - | 0
|  | 40172 | Reserved | 2
|  | 40174 | Reserved | 2
| UnRegdN | 40176 | Unregister the node. Writing a value of 100 will unregister node 100, 101 will actively unregister node 101 etc. | 1 | - | C3 | USHORT | - | NV | No | RW | - | - | - | 0
| RadioRecvrSensty | 40177 | Radio Receiver Sensitivity. It is used with RSSI to calculate the Fade Margin. | 1 | - | C3 | SHORT | - | NV | No | RW | - | - | - | 102
|  | 40178 | Reserved | 7 |  |  | USHORT
| AlmGen | 40185 | 0 - Alarm will be genearted if current raw data is not in the Alarm Raw Min/Max range 1- Alarm will be generated if current EU data is not in the Alarm EU Min/Max range | 1 | - | C3 | USHORT | - | NV | No | RW | - | - | - | 0
| ResetOOR | 40186 | Reset the Out of range node parameters i.e. IR 6332 - 6362. | 1 | - | C3 | USHORT | - | NV | No | RW | - | - | - | 0
| ResetRjtdSerNum | 40187 | Reset the Rejected serial numbers i.e. IR 6363 - 6383 | 1 | - | C3 | USHORT | - | NV | No | RW | - | - | - | 0
|  | 40188 | Reserved