## Slide 1: EtherNet/IP Book of Knowledge
Answer ID 57174
September 2015

## Slide 2: Introduction
The purpose of this section of the EtherNet/IP Book of Knowledge is to point out information in “notes” type of sections that may be new or useful in regards to:
  Networking
  Switches
  Messaging and communications

## Slide 3: Network Notes

## Slide 4: Converged Plant-wide Ethernet
Guides for recommended network designs
Based on standard design methodologies
Developed by Rockwell Automation and Cisco
Publications on
  Network Design and Security
  Wireless
  NAT
CPwE - Ethernet Network Design and Security

## Slide 5: Converged Plant-wide Ethernet
Located at
  www.ab.com
  Go to Literature Library
  Search for “cpwe” to see available documents
CPwE documents posted on Literature Library

## Slide 6: Converged Plant-wide Ethernet
Deploying Network Address Translation
    ENET-WP036
    ENET-TD007
Identity Services
    ENET-WP037
    ENET-TD008
Securely Traversing Data across the Industrial Demilitarized Zone
    ENET-WP038
    ENET-TD009
Some Examples

## Slide 7: Device Level Ring (DLR) - References
The EtherNet/IP Embedded Switch Technology
  Covers DLR
    http://literature.rockwellautomation.com/idc/groups/literature/documents/ap/enet-ap005_-en-p.pdf
Embedded Switch Technology Reference Architectures
  Shows supported network layouts for two port devices
    http://literature.rockwellautomation.com/idc/groups/literature/documents/rm/enet-rm003_-en-p.pdf
Ethernet Design Considerations
  General guide to EtherNet/IP and devices
    http://literature.rockwellautomation.com/idc/groups/literature/documents/rm/enet-rm002_-en-p.pdf

## Slide 8: CIP Sync
Uses IEEE 1588-2008 PTP standard
Allows time synchronization between devices within 100ns accuracy
Enable in devices and switches when used
Detailed in:
    Publication - http://literature.rockwellautomation.com/idc/groups/literature/documents/at/ia-at003_-en-p.pdf
    Answer ID - 623577
PTP - Precision Time Protocol

## Slide 9: Vlans
Vlans are one way to segment large networks into manageable, isolated groups
  A single network with thousands of devices can be virtually impossible to maintain
  One single mistake or device malfunction could potentially affect all devices
May need router or a switch with some level of routing capability to cross Vlans
A general practice is to limit each network or Vlan to 255 nodes or less (Class C networking)

## Slide 10: Stratix Notes

## Slide 11: Networking Line-Up
Various network products available
  Switches
  Routers
  NAT
Visit website to see available items
    http://ab.rockwellautomation.com/Networks-and-Communications/Ethernet-IP-Network

## Slide 12: Stand Alone Nat Devices
1783-NATR
    Use simple 1:1 Network Address Translation (NAT) to map IP addresses on the machine subnet to IP addresses on the control network (support for up to 32 translation mappings)
    Support both Linear and Device Level Ring (DLR) topologies on the machine network
9300-ENA
    Provide Ethernet IP Address translations for up to 128 devices
    Include an Embedded Network Discovery Tool with a DHCP Server for analysis and configuration of local network devices
    Offer SD card support for initial configuration and backup/restor

## Slide 13: 5K & 8K Routing Options
Static routing supported
  Manually configured
Connected routing supported
  All connected Vlans must have IP interface configured on one switch
Dynamic routing supported in select versions
  Uses routing protocol to build routing tables
See manual for more information:
  http://literature.rockwellautomation.com/idc/groups/literature/documents/um/1783-um007_-en-p.pdf
Stratix 5k/8k switches support routing (except 5100 wireless)

## Slide 14: DLR Configuring Stratix 5400/5700
Can be enabled through web browser (Device Manager)

## Slide 15: DLR Configuring Stratix 5400/5700
Choose Supervisor
Choose desired ports
Unless instructed otherwise, leave:
  Interval at 400us
  Timeout at 1960
  Precedence at 0
  Vlan id at 0

## Slide 16: Stratix 5K & 8K RSLinx Directed Broadcast
RSLinx directed broadcasts need to be allowed by the switch. Use the Ethernet/IP driver in RSLinx and configure it similar to the following assuming the devices are on a 192.168.1.x network
Use the ip routing and ip directed-broadcast CLI command on the switch to enable remote broadcasts on the Vlan with the devices to be browsed

## Slide 17: Stratix 5K & 8K Port Status
Can check port status via device manager Dashboard
Can also check port status via CLI
  Show ip int brief
    Port should say Up Up if operating

## Slide 18: Multicast Notes

## Slide 19: Multicast - IGMP Control
Select IGMP Snooping on all switches
Enable IGMP querier on all v2 switches
  Note: With version 2, all the switches will negotiate and the lowest IP address will be the IGMP querier. IGMP v1 enabled queriers will not negotiate, so avoid v1 queriers
Recommendations

## Slide 20: Multicast - IGMP Querier Compatibility
Version 1
  Uses a fixed querier
  While there are joins, there are no leaves. Groups leave by timeout
Version 2
  Is a superset of version 1. Version 2 added a Leave function whereas v1 handled this with a timeout
  Multiple queriers will negotiate
  Interoperability between v1 and v2 includes consideration of a number of factors such as the network mix of querier version and host IGMP version. However, there are some simple statements such as IGMPv1 multicast consumers will work with IGMP v2 queries
Version 3
  As with V2, V3 queriers should be backwards compatible with V1 and V2 multicast consumers
Recommendations

## Slide 21: CIP and TCP Timeout Notes

## Slide 22: CIP and TCP Timeouts
Without any activity, TCP connections will close in about 2 minutes
Closing TCP connections sooner, could be desirable for different reasons
  TCP keep-alives will reduce the network bandwidth on a slow link (19.2Kbaud, VPN, Wireless)
  Reduce bandwidth in case there is a monetary charge for data

## Slide 23: CIP and TCP Timeouts
MSG timeout
    User configurable - Default 30 seconds
TCP retransmission timers
    Not user configurable - Retransmission occurs if a TCP ACK is not received
TCP keep-alive timer
    Not user configurable - Occurs if there is no TCP traffic (user or retransmission)
CIP inactivity timer
    User configurable (in MSG path) for unconnected CIP messages
    Effectively closes a TCP connection if no activity
There are 4 timers associated with MSG instructions

## Slide 24: CIP and TCP Timeouts
CIP inactivity timeout to close TCP connection
    The CIP inactivity timeout can be configured in 1 sec increments from 1 sec to approx 120 sec. This can be specified in the MSG Path of the TCP originator. The default is 120 seconds. See next slide for an example
    If this timeout occurs, the TCP connection will be closed by the originator
    If this timeout is specified in a CIP connected MSG, it is ignored
    If this timeout occurs but the MSG has not yet received a response, the MSG will error at the MSG timeout specified
    NOTE: MSG instruction timeout - When a MSG (CLGX, CPX) times out, it does not close a TCP connection

## Slide 25: CIP and TCP Timeouts
TCP inactivity timeout (CIP connected or CIP unconnected)
    Not user configurable
    If no data is sent, keep-alives will be periodically sent
    If no data is sent or received in 120 sec, either side may close the connection.

## Slide 26: CIP Inactivity Timer To Close TCP Connection
Example of setting the CIP message inactivity timeout configuration. This timeout is valid only for unconnected MSGs. Screen capture below copied from Rockwell knowledge base document 22644
If this timeout occurs, the MSG will error (0x204) at the specified MSG timeout
The Ethernet module does not inform the controller of the inactivity timeout. This timer begins when MSG.EN = 1

## Slide 27: TCP Connection Timeouts
1756-EN2x diagnostic shows default TCP timeout

## Slide 28: 1756-EN2T Notes

## Slide 29: Current En2x I/O Capacity
This curve with EN2x release 3 or later and L7 controller
Notes: Enhanced CLGX Ethernet modules;
1756-EN2T/C, EN2TR/B, EN2F/B, EN3TR/A, EN2TXT/C

## Slide 30: 1756-EN2x CPU Utilization
Max I/O packet rate
(pkt rate at 100% utilization depends on packet sizes)
I/O % Utilization
CPU% available for HMI
CPU % module total
Packets/second
CPU utilization is a combination of I/O and HMI
With 100% I/O utilization, there is still module capacity for HMI.
Max I/O pps = f(RPI, size) for each connection
CPU% in use for I/O
100 %
With 100% I/O utilization, there is still module capacity for HMI.

## Slide 31: Open Sockets
Allows use of more protocols
User code required
Sockets manual
    ENET-AT002
Knowledgebase has many examples, such as:
    Answer ID 33672 - 1756-EWEB Open Sockets Server Application sample
    Answer ID 50122 - Example Add On Instructions for Sockets

## Slide 32: EtherNet/IP Book of Knowledge