## Slide 1: EtherNet/IP Book of Knowledge
Network and Device Troubleshooting

## Slide 2: Agenda
Analyzing Traces
Traffic Capture
Port Mirroring
Some Basics

## Slide 3: Some Basics Why do we do this?
Errors in the I/O tree
Poor performance
Intermittence communication
Timeouts

## Slide 4: Some Basics Before Wireshark
Port settings
  Auto vs. forced
  Speed and duplex
Diagnostics (web pages
  Media counters
  Missed I/O
  CPU
Packet capture may not be needed!
Before asking for a capture……..first check

## Slide 5: Some Basics Forced Vs. Autonegotiate
Autonegotiate is the default setting on devices and switches
  Used in most applications
  Unmanaged switches use auto
  Uses handshaking to determine fastest supported settings
  May decrease to 10mb in noisy environments (and will stay there until next powercycle/cable disconnect)
Autonegotiate is default setting
Which one should be used?

## Slide 6: Some Basics Forced Vs. Autonegotiate
Forced takes time and effort to program the ports. Some applications require forced setting
  Quick Connect (to eliminate handshaking time)
  Noisy Environments (to stay at 100mb)
  Becomes an issue when replacing equipment if forced is not set (since auto is the default)
Forced is manually set
Which one should be used?

## Slide 7: Some Basics Match Port Settings For Each Link
Make sure port settings on each end of an Link (Ethernet cable) match
  Otherwise a duplex mismatch will occur which may cause communication errors
Different ports on a switch (or a device) are not required to match and may be set differently
Both ends of a cable must match!
Avoid half duplex unless required by device, half duplex is slower

## Slide 8: Some Basics Duplex Mismatch
Check settings and media counters
Autonegotiate will go to Half Duplex when connected to another port that is forced
  Media errors can happen on both of these devices causing lost, delayed, and retransmitted packets

## Slide 9: Some Basics Diagnostics
Diagnostics viewable in various areas
  Web pages of devices
  RSLinx
  Switches
  HMI – Ethernet Diagnostics Faceplate

## Slide 10: Some Basics Bad Cables
Sometimes switches can detect bad cables
Bad cables cause lost and retransmitted packets
Use a decent cable checker or try replacing cable
Intermittent network issues are often caused by mismatched ports or bad cables

## Slide 11: Some Basics Bad Cables
Bad cables that cause frequent intermittent errors can break a DLR network.
  Bad cable anywhere on the network may cause a DLR rapid fault
  After DLR rapid fault, the bad cable may cause devices to drop off
  Check media errors on all devices
  Capture may show missing packets
  Can be difficult to track down

## Slide 12: Some Basics Lost Packets
Check if CPU loading on devices is greater then 90%
  Spikes in traffic may overwhelm device
For I/O, check missed packets
  If there are missed IO packets, start checking on media errors on all points between devices

## Slide 13: Some Basics Lost Packets
Bridged connection may indicate which network paths to check
  Look at missing packets counters
    Which devices do they belong?
    Where on the network are those devices?

## Slide 14: Some Basics Module Rejects
“Rejects” means that the Logix Ethernet module hardware passed an I/O packet to the firmware but the firmware looks at the packet and then dropped it. This increments the Reject diagnostic and also counts toward CPU usage. Rejects will occur for the following reasons:
    Duplicate multicast streams
    The firmware enables module hardware to accept specific multicast groups. The hardware cannot distinguish duplicates.
    Recommendation: Avoid duplicate multicast groups by having less than 1025 nodes on a network.
The hash table (hardware) is not perfect
    Resulting in some multicast being past to the module firmware.
    Recommendation: None.
A network event disrupts traffic. The consumer times out and closes the connection. The data producer has not yet timed out. Then, the absent stream starts arriving at the consumer again because the network is now working good. The restarted stream will be rejected by the consumer because there no longer is a CIP connection open with that connection identifier.
    Recommendation: None.
All three of the above are the similar in that the firmware can’t associate a received packet with an active CIP connection ---- it's rejected .

## Slide 15: Some Basics HTTrack
HTTrack software allows gather all the web pages from a device and from multiple devices quickly and easily
Answer ID 67297 How to capture diagnostic webpages from Ethernet devices

## Slide 16: Some Basics HTTrack
Web pages are gathered in a format easily viewed and navigated
  Does not work with 1734-AENT(R) or Stratix 5700/8000
Folder can be easily zipped and emailed

## Slide 17: Some Basics EtherNet/IP Diagnostics Faceplate
Quickly gather diagnostics in one location
Available on sample code website
Notes: The EtherNet/IP Diagnostics Faceplate allows commonly used diagnostics data to be collected and easily viewed for up to 50 devices.
Faceplates are available for both SE and ME.
Proactive tool to detect network and device communication errors.

## Slide 18: Some Basics EtherNet/IP Diagnostics Faceplate
Monitors up to 50 devices
Automatically detects and shows supported diagnostics such as media errors, missed I/O, and link status

## Slide 19: Some Basics Summary
Duplex mismatch or bad cable results in the following
  Slower communication
  Lost packets
  Lost connections
  Intermittent issues
These show up in diagnostics as
  Media counters
  Missed I/O
  CIP connection timeouts

## Slide 20: Agenda
Analyzing Traces
Traffic Capture
Port Mirroring
Some Basics

## Slide 21: Port Mirror - Stratix 5700/8000/8300 Multicast
Some switches, like the Stratix 5700 and 8000 series and other Cisco switches, do not mirror multicast control traffic (Leave and join Group messages)
  This can complicate multicast connection troubleshooting and make it difficult to find switch or device issues
It is recommended when possible to use an 1783-ETAP or other capture device to capture traffic if multicast IO connection loss is being investigated
NOTE for Multicast!

## Slide 22: Port Mirror - Stratix 5700/8000/8300 Multicast
DLR versions of Stratix 5700 switches do not mirror the DLR control traffic.
If mirroring DLR control traffic is desired, use an ETAP
NOTE for DLR!

## Slide 23: Port Mirror - Stratix 5700/8000/8300 Device Manager
Can use web page (Device Manager) of Stratix to configure port mirror for Stratix 5700/8000/8300
Web page requires that the cable to be disconnected from the port to be used as the mirror during configuration

## Slide 24: Port Mirror - Stratix 5700/8000/8300 Device Manager
To configure:
  Select Smart Ports
  Select port to be used as mirror, and select Edit
  Select Source Interface
  If desired, select Ingress Vlan
    If using HMI or other communications software on the computer that is needed at the same time the port mirror is being done. Otherwise, leave Ingress Vlan as none

## Slide 25: Port Mirror - Stratix 5700/8000/8300 CLI
Port mirror can also be done via CLI
PuTTY is a popular free CLI client
Fill in:
  IP address
  Port 23
  Telnet
PuTTY or other telnet client for CLI (Command Line Interface)

## Slide 26: Port Mirror - Stratix 5700/8000/8300 CLI
To mirror a port with no ingress
  monitor session 1 destination interface fa2/7
  monitor session 1 source interface fa2/3 both
To mirror all Vlan traffic
  monitor session 1 destination interface fa2/7
  monitor session 1 source Vlan 192 both
    Note – for high traffic, check port utilization to make sure port is not at 100%
To see how port mirror is configured
  show run | section monitor
To stop mirror
  no monitor session 1
Some mirror command examples

## Slide 27: Port Mirror - Stratix 5700/8000/8300 CLI
Following two lines show commands to set up mirror. The ingress vlan is optional
  monitor session 1 source interface fa1/1
  monitor session 1 dest interface fa1/8 ingress vlan 192
Sessions 1 and 2 available

## Slide 28: Port Mirror - Stratix 5700/8000/8300 CLI
Show monitor can also be used to see current mirror setup
  In non config mode, show monitor
  In config mode, do show monitor

## Slide 29: Port Mirror 1783-ETAP
To configure an ETAP for mirroring, use RSLinx Device Configuration
  Check Enable Device Port Debugging Mode
  Uncheck all other options as shown below

## Slide 30: Port Mirror Stratix 6000
Select both IN and OUT a port in the Mirror From column
Select the Capture to Port
Select Enabled for the Mirror Configuration drop down

## Slide 31: Agenda
Analyzing Traces
Traffic Capture
Port Mirroring
Some Basics

## Slide 32: Traffic Capture Multiple Network Interface Cards?
Does the computer have multiple Network Interface Cards (NIC)?
If so, know which one is being used since they will show up as options in Wireshark
Can disable other NICs via right click
  Control Panel -> Network and Sharing -> Change adapter settings

## Slide 33: Traffic Capture Firewalls
Make sure that if the computer being used to capture traffic, has the vpn / firewall / security software disabled, or check with IT that it will not interfere with the capture
  Otherwise, a trace may be missing important information and may not be useful
NOTE for Firewalls!

## Slide 34: Traffic Capture Using Wireshark
To start a capture in Wireshark
  Select the Capture menu

## Slide 35: Traffic Capture Using Wireshark
In the capture menu:
  Select the NIC to use
  Select Options

## Slide 36: Traffic Capture Using Wireshark
In the Options window, make sure:
  Promiscuous is checked and Capture Filter is empty
    This is important to preserve all information!
  If a rolling log is desired for long captures, fill similar to that shown
  Display Options are as checked

## Slide 37: Traffic Capture Using Wireshark
Leave Wireshark running until a minute or more after the event that is being investigated
Make sure to “Stop” the capture first
Save the capture after stopping it

## Slide 38: Traffic Capture Using Wireshark
Switches and routers
Sometimes two simultaneous captures are needed!

## Slide 39: Traffic Capture Coloring Rules
Answer ID 491368 has coloring rule attachment.
  Normal CIP traffic in shades of blue or black
  Retransmission highlighted in yellow
  CIP errors highlighted in red
  ICMP errors and STP changes in red
To import coloring rules
  -> View -> Coloring Rules
  -> Delete current rules
  -> Import new rules
Coloring rules can be used to visually point possible CIP issues
Coloring rules can help when looking traces

## Slide 40: Traffic Capture Coloring Rules
Coloring rules can help show if CIP traffic was captured

## Slide 41: Traffic Capture Coloring Rules
Filtering in Wireshark can also help point out if expected packets can be found.
“ENIP” for RSLinx browse and I/O
“CIP” for RSLinx HMI comms and messaging
Answer ID 491368 has more filters

## Slide 42: Traffic Capture Is The Trace Useful?
Empty traces have been taken (unknowingly)
To avoid wasted effort due to empty traces, it helps to know what a trace should look like
Does the trace have useful information or is it empty?

## Slide 43: Traffic Capture Is The Trace Useful?
Filter on “ip.addr eq 192.168.1.76 and ip.addr eq 192.168.1.226”
  Use your IP addresses
  CIP Traffic should be flowing in both directions
  Wireshark does not decode all CIP commands and may show as unknown service – this is ok
  Protocol can be CIP or CIP CM
  Series of CIP request followed by replies
    Replies are usually “Success”
HMI and Message Traffic

## Slide 44: Traffic Capture Is The Trace Useful?
HMI and Message Traffic example picture
  Requests coming from HMI (226), and replies are being sent back (from 76)
  CIP or CIP CM protocol in both directions

## Slide 45: Traffic Capture Is The Trace Useful?
General I/O traffic should have ENIP packets
  Filter on ENIP
  ENIP traffic from I/O module will be going to multicast address of 239.x.x.x if unicast not checked, or to the controller address otherwise
  Controller will send packets directly to I/O module
  ENIP packets also have ID’s and sequence numbers

## Slide 46: Traffic Capture Is The Trace Useful?
I/O data from specific node
  ENIP data is flowing too and from the I/O node (91)
  May need to filter on ip.addr == 192.168.1.91 to hide other traffic

## Slide 47: Traffic Capture Is The Trace Useful?
This is a “good” trace of a device error.
  Show Forward open to device
  Device complains about a conflict
    May be shown as an error in the I/O tree
    RSLogix 5000 ->I/O tree -> module properties -> connections tab

## Slide 48: Traffic Capture Is The Trace Useful?
If we want a trace of node 192.168.1.10…… the below trace does not show any traffic coming or going to that node, check port mirror setup
  This trace only shows broadcast type traffic
  No point to point or multicast traffic

## Slide 49: Traffic Capture Is The Trace Useful?
The below could be a trace of mirroring more then 1 port.
  Lots of duplicate packets indicated by Wireshark of two remote devices – more difficult to analyze, but sometimes possible

## Slide 50: Traffic Capture Is The Trace Useful?
The below may be the result of mirroring more then 1 port.
  Lots of duplicate IO packets right next to each other
  More difficult to figure out the trace

## Slide 51: Traffic Capture Is The Trace Useful?
In this example, there is a lack of any traffic except multicast
  May be due to forgetting port mirror or mirroring wrong port
  This trace may not be useful
  Try ““ip.addr eq x.x.x.x and ip.addr eq y.y.y.y”
    to see if there is any traffic going back to the I/O module.

## Slide 52: Agenda
Looking At Traces
Traffic Capture
Port Mirroring
Some Basics

## Slide 53: Looking At Traces General Questions
How does TCP work?
What does a normal or standard Ethernet frame like?
How is Ethernet traffic managed?
What is an ARP table?
How was Ethernet developed?
What is a Vlan tagged packet?
What are SYN packets?
What is a Vlan?
What is CAT6?
Internet searches are you friend! Don’t be afraid to use them!!!!
Where can I find answers to general Ethernet questions?

## Slide 54: Looking At Traces ODVA CIP Spec
When analyzing traces, It’s often necessary to have the licensed CIP specification which describes the expected format of packets and information flow

## Slide 55: Looking At Traces ODVA CIP Spec
Error codes listed in CIP Spec

## Slide 56: Looking At Traces ODVA CIP Spec
CIP Information that all devices depend on in CIP Vol 1
Examples
  Generic I/O
  Forward Opens

## Slide 57: Looking At Traces ODVA CIP Spec
QOS, Forward open, etc., for Ethernet described in CIP Vol. 2
CIP Safety specification in Vol. 5

## Slide 58: Looking At Traces Data Access manual
Logix5000 Data Access manual
  Describes public read/write methods
  Can sometimes be helpful for 3rd party HMI traces
  Located on Literature Library
RSLinx (Classic and Enterprise) sometimes use undocumented methods

## Slide 59: Looking At Traces Coloring Rules
Answer ID 491368 has coloring rule attachment.
  Normal CIP traffic in shades of blue or black
  Retransmission highlighted in yellow
  CIP errors highlighted in red
  ICMP errors and STP changes in red
To import coloring rules
  -> View -> Coloring Rules
  -> Delete current rules
  -> Import new rules
Coloring rules can be used to visually point possible CIP issues
Coloring rules can help when looking traces

## Slide 60: Looking At Traces CIP uses TCP/IP and UDP/IP
TCP guarantees packet delivery and data order
  Packets contain sequence number
  TCP tries to keep connection open by resending data if it does not get an ack (lost data) and will wait before sending additional data
TCP/IP stands for
  Transmission Control Protocol / Internet Protocol
TCP/IP

## Slide 61: Looking At Traces CIP uses TCP/IP and UDP/IP
UDP does not guarantee delivery
  Up to application to check
  Sent once, not verified by sender
UDP/IP stands for
  User Datagram Protocol / Internet Protocol
I/O data uses UDP/IP

## Slide 62: Looking At Traces CIP uses TCP/IP and UDP/IP
Unicast
  UDP and TCP
    I/O data (port 2222)
    CIP (port 44818) - HMI, Controller messaging, programming, creating I/O connections
Multicast
  UDP only
    I/O data (port 2222)
      Needs switch management IGMP on large networks
Broadcast
  UDP only
    RSLinx browse (port 44818)

## Slide 63: Looking At Traces IEEE and ODVA
List Identity replies
  Can usually determine product manufacturer from MAC address or from the Vendor ID of the reply from Wireshark display
  IEEE has MAC ranges, ODVA had Vendor ID list, (search internet)

## Slide 64: Looking At Traces ARP
ARP stands for Address Resolution Protocol
  ARPs are a necessary part of traffic. It’s how devices associate MAC addresses to IP Addresses to find each other
  Will show up periodically, this is normal
  Can be filtered with “arp” or “!arp”

## Slide 65: Looking At Traces ARP
ARPs are a layer 2 message that imbed IP addresses as data to find MAC addresses of local devices
  Broadcast range is FF:FF:FF:FF:FF:FF
  ARPs can be device to device or broadcast
  Remote IPs use MAC address of router
  ARPs are only for local subnet

## Slide 66: Looking At Traces ARP
Module may ARP for a missing device (powered off for example) about once a second
Module may ARP for device it is communicating with 1 or 2 times a minute
If a module is ARPing and IP address at a much greater frequency (10’s or more a second), take a closer look to see if device issue
If there is lack of communication, investigate the unanswered ARPS

## Slide 67: Looking At Traces ARP
What does IP Device tracking look like?
See Answer ID 568750 for needed changes to switch config

## Slide 68: Looking At Traces DLR
DLR beacons and announce frames are a normal part of DLR ring traffic mirrored by ETAP
  Can be filtered with “dlr” or “!dlr”
  Uses Vlan tags (802.1Q) which will usually get blocked by managed switches if plugged directly into ring
  All beacon packets have same source and dest mac addresses

## Slide 69: Looking At Traces VLAN tags
Some NIC cards and Windows settings can strip VLAN tags from packets.
ETAP does not strip the VLAN tags.
Used in DLR beacons
  As well as some other protocols
  And switch Trunk traffic

## Slide 70: Looking At Traces A Normal I/O Trace
This is a normal I/O trace of one I/O device during power up
  Devices ARP, create a TCP connection, open a CIP connection, and send CIP communications

## Slide 71: Looking At Traces A Normal I/O Trace
Multiple ARPs happen on power up
“Who has….tell 0.0.0.0” is for duplicate IP detection
Gratuitous ARPs announce that device is available

## Slide 72: Looking At Traces A Normal I/O Trace
Controller ARPs for I/O hardware address

## Slide 73: Looking At Traces A Normal I/O Trace
TCP opened
  SYN(synchoronize) request to port 44818
  SYN/ACK back from port 44818

## Slide 74: Looking At Traces A Normal I/O Trace
Register session
  Contains session handle, used in all CIP TCP traffic
  Req ID is ignored, Rsp ID should be non zero

## Slide 75: Looking At Traces A Normal I/O Trace
Forward Open and response
  Forward open contains serial number, Connection ID’s, RPIs, and more.
  Serial number used when a forward close is issued (not the ID’s)

## Slide 76: Looking At Traces A Normal I/O Trace
I/O is sent from port 2222 to port 2222
ID’s are unique within an device (a singular IP address)
Sequence number starts at 0 or 1 and increments by 1

## Slide 77: Looking At Traces I/O Timeouts
Timeout is indicated in the connection forward open packets
  Also shown on the bridge connections of EN2T
I/O standard uses a binary multiplier starting at 4 (4,8,16,32,64,128) times the RPI to define a timeout value over and closest too 100ms
    Example: an RPI of 15 ms * 8 = 120 ms timeout value
    Example: an RPI of 25 ms * 4 = 100 ms timeout value
    Example: an RPI of 3 ms * 64 = 192 ms timeout value
    ControlLogix Redundancy output timeouts may be double (over 200ms)
I/O safety timeout is define by user application from the I/O tree
I/O data uses UDP/IP

## Slide 78: Looking At Traces Analyzing I/O packets
Add the connection ID column as shown below.
  Make connection ID sorting and search easier
  Can use new column with right click functionality

## Slide 79: Looking At Traces I/O Graph
Wireshark I/O graph can be used to see what the capture packet rate is while the capture is running or on a saved file
  Expected rate depends on traffic being captured
  Sometimes can be useful to find problem areas

## Slide 80: Looking At Traces Conversation Filters
Conversation filter filters for 2 specific devices
  MAC address
  TCP
  IP

## Slide 81: Looking At Traces Run bit
If forward open is in the trace, Wireshark might be able to parse out the run bit from the output packets (from controller to I/O)
  Only some I/O devices use this format
  Device should only use data when run bit is on

## Slide 82: Looking At Traces Multicast Recommendations
With latest releases, unicast can be used for I/O and produce/consume tags
If multicast is used, select IGMP Snooping on all switches
Enable IGMP querier on all switches that support v2 or later. With IGMP version 2 or later, all switches will negotiate and the lowest IP address will be the IGMP querier.
Note: IGMP v1 enabled queriers will not negotiate and should not be enabled at the same time. If there are no v2 queriers, use only one v1 querier

## Slide 83: Looking At Traces Multicast
If multicast I/O connections drop, the Ethernet module will issue an IGMP leave message
  Note: Some switches, like the Stratix 8000, do not mirror leaves and joins (group). It is recommended to use ETAP to capture traffic. May be needed to investigate the UDP multicast traffic flow
If a module joins a group, it will send a group message
When multicast I/O connections exist, the Ethernet module will issue an IGMP “Membership Report group” message for each “Membership Query”

## Slide 84: Multicast - IGMP Leave happens when?
Case 1: Startup
  When a consumer receives a successful Forward Open reply for a multicast group, the consumer starts sending heartbeats and also sends an IGMP Join.
  If the first multicast is not received in 10 seconds, the consumer sends an IGMP Leave.
  The consumer considers the CIP connection as timed out and stops sending unicast.
  Examples of timeouts after the first data:
    A 2ms RPI has a CIP connection timeout of 128ms. Then, X >128ms.
    A 100ms RPI has a CIP connection timeout of 400ms. Then, X > 400ms.
A Logix Ethernet module sends an IGMP Leave when all CIP connections through that module are broken for the multicast address being consumed.

## Slide 85: Multicast - IGMP Leave happens when?
Case 2: Two controllers consuming same tag thru same ENxx
  At the consumer Logix chassis, if there are 2 consumer controllers for the same tag and both are consuming thru the same ENBT module, then that ENBT will send a Leave for that multicast group when both Logix controllers no longer want to consume that group. A Logix controller will not consume under the following conditions:
    Consumed tag is inhibited or deleted
    I/O connection is inhibited or deleted

## Slide 86: Multicast - IGMP Leave happens when?
Case 3: Tag producer dies/disconnected/disappears
  At the consumer Logix chassis, if the tag producer is disconnected or the infrastructure (switch) fails, the consumer Ethernet module no longer detects the produced tag and the CIP connection will close.

## Slide 87: Multicast - IGMP Leave happens when?
Case 4: Duplicate multicast address
    Consider the case of 2 Logix controllers each consuming data from different data producers. And, each data producer transmits its data using the same multicast address. This is allowed in the EIP spec because each multicast stream includes unique information that differentiates.
    If 2 or more multicast producers are using the same multicast address, the consumer ENBT module will not send a Leave until all consumer Logix controllers no longer want to receive that multicast group.

## Slide 88: Looking At Traces Multicast
Here is picture with filter “IGMP” of a connection being broken and remade

## Slide 89: Looking At Traces Finding Connection IDs
For analysis:
The two connection IDs associated with each CIP connection need to be identified. These can be obtained from a EN2T web page. To make them available dynamically in Wireshark, configure a web browser (ex. Internet Explorer) to read the EN2T page shown below.

## Slide 90: Looking At Traces Finding Connection IDs
For analysis:
After a Wireshark capture is obtained, you need to learn the I/O connection IDs that were valid prior to an I/O connection loss. To do this:
Set a filter in Wireshark
TCP and ip.src==IP_of_IE_pc and ip.dst==IPofTheEN2T and tcp.seq==0
Example: TCP and ip.src==192.168.1.250 and ip.dst==192.168.1.200 and tcp.seq==0
2. Examine the first TCP packet in the TCP/HTTP sequence prior to the loss.
Below, notice the 1 second interval between 1.663 and 2.763

## Slide 91: Looking At Traces Finding Connection IDs
Now, with that packet select Analysis and Follow TCP Stream
Then, select Raw and Save as an html file.
Then, open the html file with a web browser such as Internet Explorer (see next page).

## Slide 92: Looking At Traces Finding Connection IDs
These connection IDs can then be used in a Wireshark filter to monitor packet flow from source to destination.

## Slide 93: Looking At Traces Message Instruction
Example of setting the CIP message inactivity timeout configuration. This timeout is best used with unconnected MSGs. Screen capture below copied from Rockwell knowledge base document 22644
    If a timeout occurs, the MSG will error (0x204) at the specified MSG timeout
    The Ethernet module does not inform the controller of the inactivity timeout. This timer begins when MSG.EN = 1

## Slide 94: Looking At Traces Message Instruction
Sample capture of traffic with timeout set to 5 seconds
TCP Reset happens after 5 seconds to close the TCP connection
Reduces or eliminates keeps alive TCP traffic

## Slide 95: Looking At Traces Message Instruction
Sample capture of traffic with timeout set to 55 seconds
  Notice the keep alive traffic
  Timeout will happen after 120 seconds of not activity if it is not specified

## Slide 96: Looking At Traces Malformed packets
Wireshark might show packets as malformed when they are not
  Packets tagged as bad checksum may be due to NIC hardware offloading (Checksum changed or zeroed by hardware)
If many packets of interest show this, then disable checksum checking.
  In Wireshark, click on Edit  Preferences  Protocols  TCP (or UDP)  (Uncheck) Validate TCP (or UDP) checksum if possible

## Slide 97: Looking At Traces Malformed packets
Packets in Wireshark tagged as Malformed might not be
  The below picture shows a “Malformed” TCP packet.
  This is actually a CIP packet that is not being parsed correctly.
  Port 1090 is associated with ff-fms fieldbus and is incorrectly decoded
For this example, to change this behavior, follow these steps:
  Click on Analyze  Enabled Protocols  Scroll down to FF (or whatever protocol is indicated by the port)  Uncheck the box  Apply
  Wireshark should then decode based on the other port which in this case is 44818 which is what CIP uses

## Slide 98: Looking At Traces Malformed packets
Packets in Wireshark tagged as Malformed might not be
  The below picture shows a “Malformed” IO packet.
  This is actually an input only connection that does not have a run/idle 32bit header, but Wireshark assumes connections have 32bit header
For this example, to change this behavior (if desired), follow these steps:
  Click on Edit -> Preferences -> Protocols -> ENIP -> uncheck Dissect 32-bit header in the O->T direction
  Wireshark will then not try to decode the packet and will not flag it with an error

## Slide 99: Looking At Traces Window Size
If a device stops sending data, check the window sizes
  If window size starts above 2k, but then is decreasing and stays below 2k, then the other side may not be reading it’s data. In this case, investigate the device whose buffer is not recovering.

## Slide 100: Looking At Traces ICMP Packets
ICMP error packets usually indicate a problem
In this example, RSLinx was shut down, and computer replies that packet cannot be processed since RSLinx shut down the port

## Slide 101: Looking At Traces QOS
Some devices do not support QOS
  Zero value in QOS field
  Supposed to accept packet if receiving QOS packet
Some devices support QOS
  Non zero value in QOS field

## Slide 102: Looking At Traces Duplicate packets?
Duplicate packets can happen if:
  Device issues
    Device does not ack
  Network issues
    Packets get duplicated on network

## Slide 103: Looking At Traces Duplicate packets?
Duplicate packets could be cause by the way the mirror was done and are not duplicate in the network and may actually be expected
    Example: Only packets coming from node 226 are getting duplicated. The computer has RSLinx and Wireshark. RSLinx is communicating with device.

## Slide 104: Looking At Traces Removing Duplicate Packets
Can get rid of duplicate packets with editcap.exe
Example:
  C:\Users\<user>\Desktop\Wireshark training\Traces>"c:\Program Files\Wireshark\editcap.exe" -d input_file.pcapng output_file.pcapng

## Slide 105: Looking At Traces Routing between Vlans
VLANs and routers get in the middle if devices are not on the same subnet
  Packets get layer 2 mac address of VLANs
  Example shows router at address 192.168.1.5

## Slide 106: Misc Tips Routing between Vlans
View mac addresses learned on switch with CLI
  Show mac address-table
View the mac address of the vlan or port with CLI
  Show int vlan # (or fa1/1)
View the mac address with device web page if there is an “arp table”

## Slide 107: Misc Tips Pinging
Can you ping a device?
  At prompt “ping <ip address>”
What devices are there?
  Ping all IP addresses in subnet in a Windows prompt
  C:\>for /l %lastoctect in (1,1,254) do @ping 192.168.1.%lastoctet -n 1 -w 100 | find "Reply"

## Slide 108: Misc Tips Is Switch Dropping Packets?
Stratix/Cisco switches will drop Vlan tagged packets (possibly miswired DLR ring)
  “Show Interface <port>” to look for input errors
    These packets are dropped

## Slide 109: Ethernet Book of Knowledge Troubleshooting